## Modulübersicht
PWM Modul (ModNr 0 -15)					Leaflet Grundmodul
Mreg	O_Coil	I_Coil	I_Analog	O_Analog		Mreg	O_Coil	I_Coil	I_Analog	O_Analog
0	Inverted 1		Error	Freq		0	ENABLE PERI	FAULT_OUT	Error	Command Reg
1	Inverted 2			PWM_1		1	RESERVED	FAULT_HBUS24	V_Major	ClientWarn/Error
2	Inverted 3			PWM_2		2	RESERVED	FAULT_HBUS	V_Minor	RESERVED
3	Inverted 4			PWM_3		3	RESERVED	SWITCH IN 1	V_Patch	RESERVED
4				PWM_4		4	RESERVED	SWITCH IN 2	Serial Number MSB	RESERVED
REL Modul 1 (ModNr 16 – 19)					5	RESERVED	SWITCH IN 3	Serial Number	RESERVED
Mreg	O_Coil	I_Coil	I_Analog	O_Analog		6	RESERVED	SWITCH IN 4	Serial Number	RESERVED
0	Rel_1		Error_Flag	Config_Reg		7	RESERVED	ISO IN 1	Serial Number LSB	RESERVED
1	Rel_2			All_Rel		8	RESERVED	ISO IN 2	PWM	RESERVED
2	Rel_3					9	RESERVED	M_ResPin1	REL	RESERVED
3	Rel_4					10	RESERVED	M_ResPin2	TMP	RESERVED
4	Rel_5					11	RESERVED	S_ResPin3	AIO	RESERVED
5	Rel_6					12	RESERVED	S_ResPin4	RESERVED	RESERVED
6	Rel_7					13	RESERVED	RESERVED	RESERVED	RESERVED
7	Rel_8					14	RESERVED	RESERVED	RESERVED	RESERVED
TMP Modul (20-27)					15	RESERVED	RESERVED	RESERVED	RESERVED
Mreg	O_Coil	I_Coil	I_Analog	O_Analog
0			Error_Flag	Config_Reg
1			Temp_1
2			Temp_2
3			Temp_3
4			Temp_4
5			Temp_5
6			Temp_6
7			Temp_7
8			Temp_8
9			Temp_9
10			Temp_10
11			Temp_11
12			Temp_12
13			Temp_13
14			Temp_14
15			Temp_15
16			Temp_16
AIO Modul (ModNr 28 – 35)					AIO Config_Reg
Mreg	O_Coil	I_Coil	I_Analog	O_Analog	Bits	Bitname	Description
0		D_IN1	Error_Flag	Config_Reg	[15:12]	Channel D	Sets the Channel function. Default is 0 (High Imp):
1		D_IN2	%_IN_1	%_OUT_1	[11:8]	Channel C	0	Not in Use(HIGH IMP)
2		D_IN3	%_IN_1	%_OUT_2	[7:4]	Channel B	1	0-10V Output
3		D_IN4	%_IN_1	%_OUT_3	[3:0]	Channel A	2	0-10V Input
4			%_IN_1	%_OUT_4			3	0-20 mA Output
5			TEMP_1	V_OUT_1			4	0-20 mA Intput
6			TEMP_2	V_OUT_2			5	4-20 mA Output
7			TEMP_3	V_OUT_3			6	4-20 mA Input
8			TEMP_4	V_OUT_4			7	Temp Input
9			V_IN_1	I_OUT_1			8	Digital Input
10			V_IN_2	I_OUT_2
11			V_IN_3	I_OUT_3
12			V_IN_4	I_OUT_4
13			I_IN_1
14			I_IN_2
15			I_IN_3
16			I_IN_4

				37

## Discrete Output coils
				const __uint16_t MM_OutputBit_Map[][3] = {
Register Adress	Offset	Type	Mod. Nr	Registername	Values	Description		/*				Module		Mreg		Lock?			*/
1	0	LEAFLET		Peripherirals Enable	0,1			/*	0	*/	{	LEAFLET	,	0	,	1	}	,	/*	LEAFLET Module	Peripherirals Enable	*/
2	1	LEAFLET		Reserved				/*	1	*/	{	LEAFLET	,	1	,	1	}	,	/*	LEAFLET Module	Reserved	*/
3	2	LEAFLET		Reserved				/*	2	*/	{	LEAFLET	,	2	,	1	}	,	/*	LEAFLET Module	Reserved	*/
4	3	LEAFLET		Reserved				/*	3	*/	{	LEAFLET	,	3	,	1	}	,	/*	LEAFLET Module	Reserved	*/
5	4	LEAFLET		Reserved				/*	4	*/	{	LEAFLET	,	4	,	1	}	,	/*	LEAFLET Module	Reserved	*/
6	5	LEAFLET		Reserved				/*	5	*/	{	LEAFLET	,	5	,	1	}	,	/*	LEAFLET Module	Reserved	*/
7	6	LEAFLET		Reserved				/*	6	*/	{	LEAFLET	,	6	,	1	}	,	/*	LEAFLET Module	Reserved	*/
8	7	LEAFLET		Reserved				/*	7	*/	{	LEAFLET	,	7	,	1	}	,	/*	LEAFLET Module	Reserved	*/
9	8	LEAFLET		Reserved				/*	8	*/	{	LEAFLET	,	8	,	1	}	,	/*	LEAFLET Module	Reserved	*/
10	9	LEAFLET		Reserved				/*	9	*/	{	LEAFLET	,	9	,	1	}	,	/*	LEAFLET Module	Reserved	*/
11	10	LEAFLET		Reserved				/*	10	*/	{	LEAFLET	,	10	,	1	}	,	/*	LEAFLET Module	Reserved	*/
12	11	LEAFLET		Reserved				/*	11	*/	{	LEAFLET	,	11	,	1	}	,	/*	LEAFLET Module	Reserved	*/
13	12	LEAFLET		Reserved				/*	12	*/	{	LEAFLET	,	12	,	1	}	,	/*	LEAFLET Module	Reserved	*/
14	13	LEAFLET		Reserved				/*	13	*/	{	LEAFLET	,	13	,	1	}	,	/*	LEAFLET Module	Reserved	*/
15	14	LEAFLET		Reserved				/*	14	*/	{	LEAFLET	,	14	,	1	}	,	/*	LEAFLET Module	Reserved	*/
16	15	LEAFLET		Reserved				/*	15	*/	{	LEAFLET	,	15	,	1	}	,	/*	LEAFLET Module	Reserved	*/
17	16	PWM	1	Inversion PWM 1	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	16	*/	{	PWM1	,	0	,	1	}	,	/*	PWM Module 1	Inversion PWM 1	*/
18	17	PWM	1	Inversion PWM 2	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	17	*/	{	PWM1	,	1	,	1	}	,	/*	PWM Module 1	Inversion PWM 2	*/
19	18	PWM	1	Inversion PWM 3	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	18	*/	{	PWM1	,	2	,	1	}	,	/*	PWM Module 1	Inversion PWM 3	*/
20	19	PWM	1	Inversion PWM 4	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	19	*/	{	PWM1	,	3	,	1	}	,	/*	PWM Module 1	Inversion PWM 4	*/
21	20	PWM	2	Inversion PWM 1	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	20	*/	{	PWM2	,	0	,	1	}	,	/*	PWM Module 2	Inversion PWM 1	*/
22	21	PWM	2	Inversion PWM 2	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	21	*/	{	PWM2	,	1	,	1	}	,	/*	PWM Module 2	Inversion PWM 2	*/
23	22	PWM	2	Inversion PWM 3	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	22	*/	{	PWM2	,	2	,	1	}	,	/*	PWM Module 2	Inversion PWM 3	*/
24	23	PWM	2	Inversion PWM 4	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	23	*/	{	PWM2	,	3	,	1	}	,	/*	PWM Module 2	Inversion PWM 4	*/
25	24	PWM	3	Inversion PWM 1	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	24	*/	{	PWM3	,	0	,	1	}	,	/*	PWM Module 3	Inversion PWM 1	*/
26	25	PWM	3	Inversion PWM 2	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	25	*/	{	PWM3	,	1	,	1	}	,	/*	PWM Module 3	Inversion PWM 2	*/
27	26	PWM	3	Inversion PWM 3	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	26	*/	{	PWM3	,	2	,	1	}	,	/*	PWM Module 3	Inversion PWM 3	*/
28	27	PWM	3	Inversion PWM 4	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	27	*/	{	PWM3	,	3	,	1	}	,	/*	PWM Module 3	Inversion PWM 4	*/
29	28	PWM	4	Inversion PWM 1	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	28	*/	{	PWM4	,	0	,	1	}	,	/*	PWM Module 4	Inversion PWM 1	*/
30	29	PWM	4	Inversion PWM 2	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	29	*/	{	PWM4	,	1	,	1	}	,	/*	PWM Module 4	Inversion PWM 2	*/
31	30	PWM	4	Inversion PWM 3	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	30	*/	{	PWM4	,	2	,	1	}	,	/*	PWM Module 4	Inversion PWM 3	*/
32	31	PWM	4	Inversion PWM 4	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	31	*/	{	PWM4	,	3	,	1	}	,	/*	PWM Module 4	Inversion PWM 4	*/
33	32	PWM	5	Inversion PWM 1	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	32	*/	{	PWM5	,	0	,	1	}	,	/*	PWM Module 5	Inversion PWM 1	*/
34	33	PWM	5	Inversion PWM 2	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	33	*/	{	PWM5	,	1	,	1	}	,	/*	PWM Module 5	Inversion PWM 2	*/
35	34	PWM	5	Inversion PWM 3	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	34	*/	{	PWM5	,	2	,	1	}	,	/*	PWM Module 5	Inversion PWM 3	*/
36	35	PWM	5	Inversion PWM 4	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	35	*/	{	PWM5	,	3	,	1	}	,	/*	PWM Module 5	Inversion PWM 4	*/
37	36	PWM	6	Inversion PWM 1	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	36	*/	{	PWM6	,	0	,	1	}	,	/*	PWM Module 6	Inversion PWM 1	*/
38	37	PWM	6	Inversion PWM 2	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	37	*/	{	PWM6	,	1	,	1	}	,	/*	PWM Module 6	Inversion PWM 2	*/
39	38	PWM	6	Inversion PWM 3	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	38	*/	{	PWM6	,	2	,	1	}	,	/*	PWM Module 6	Inversion PWM 3	*/
40	39	PWM	6	Inversion PWM 4	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	39	*/	{	PWM6	,	3	,	1	}	,	/*	PWM Module 6	Inversion PWM 4	*/
41	40	PWM	7	Inversion PWM 1	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	40	*/	{	PWM7	,	0	,	1	}	,	/*	PWM Module 7	Inversion PWM 1	*/
42	41	PWM	7	Inversion PWM 2	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	41	*/	{	PWM7	,	1	,	1	}	,	/*	PWM Module 7	Inversion PWM 2	*/
43	42	PWM	7	Inversion PWM 3	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	42	*/	{	PWM7	,	2	,	1	}	,	/*	PWM Module 7	Inversion PWM 3	*/
44	43	PWM	7	Inversion PWM 4	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	43	*/	{	PWM7	,	3	,	1	}	,	/*	PWM Module 7	Inversion PWM 4	*/
45	44	PWM	8	Inversion PWM 1	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	44	*/	{	PWM8	,	0	,	1	}	,	/*	PWM Module 8	Inversion PWM 1	*/
46	45	PWM	8	Inversion PWM 2	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	45	*/	{	PWM8	,	1	,	1	}	,	/*	PWM Module 8	Inversion PWM 2	*/
47	46	PWM	8	Inversion PWM 3	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	46	*/	{	PWM8	,	2	,	1	}	,	/*	PWM Module 8	Inversion PWM 3	*/
48	47	PWM	8	Inversion PWM 4	0,1	This Configures the corresponding PWM Output to be inverted. Default is 0 = not inverted		/*	47	*/	{	PWM8	,	3	,	1	}	,	/*	PWM Module 8	Inversion PWM 4	*/
49	48	REL	1	Relais 1	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	48	*/	{	REL1	,	0	,	0	}	,	/*	REL Module 1	Relais 1	*/
50	49	REL	1	Relais 2	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	49	*/	{	REL1	,	1	,	0	}	,	/*	REL Module 1	Relais 2	*/
51	50	REL	1	Relais 3	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	50	*/	{	REL1	,	2	,	0	}	,	/*	REL Module 1	Relais 3	*/
52	51	REL	1	Relais 4	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	51	*/	{	REL1	,	3	,	0	}	,	/*	REL Module 1	Relais 4	*/
53	52	REL	1	Relais 5	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	52	*/	{	REL1	,	4	,	0	}	,	/*	REL Module 1	Relais 5	*/
54	53	REL	1	Relais 6	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	53	*/	{	REL1	,	5	,	0	}	,	/*	REL Module 1	Relais 6	*/
55	54	REL	1	Relais 7	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	54	*/	{	REL1	,	6	,	0	}	,	/*	REL Module 1	Relais 7	*/
56	55	REL	1	Relais 8	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	55	*/	{	REL1	,	7	,	0	}	,	/*	REL Module 1	Relais 8	*/
57	56	REL	2	Relais 1	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	56	*/	{	REL2	,	0	,	0	}	,	/*	REL Module 2	Relais 1	*/
58	57	REL	2	Relais 2	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	57	*/	{	REL2	,	1	,	0	}	,	/*	REL Module 2	Relais 2	*/
59	58	REL	2	Relais 3	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	58	*/	{	REL2	,	2	,	0	}	,	/*	REL Module 2	Relais 3	*/
60	59	REL	2	Relais 4	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	59	*/	{	REL2	,	3	,	0	}	,	/*	REL Module 2	Relais 4	*/
61	60	REL	2	Relais 5	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	60	*/	{	REL2	,	4	,	0	}	,	/*	REL Module 2	Relais 5	*/
62	61	REL	2	Relais 6	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	61	*/	{	REL2	,	5	,	0	}	,	/*	REL Module 2	Relais 6	*/
63	62	REL	2	Relais 7	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	62	*/	{	REL2	,	6	,	0	}	,	/*	REL Module 2	Relais 7	*/
64	63	REL	2	Relais 8	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	63	*/	{	REL2	,	7	,	0	}	,	/*	REL Module 2	Relais 8	*/
65	64	REL	3	Relais 1	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	64	*/	{	REL3	,	0	,	0	}	,	/*	REL Module 3	Relais 1	*/
66	65	REL	3	Relais 2	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	65	*/	{	REL3	,	1	,	0	}	,	/*	REL Module 3	Relais 2	*/
67	66	REL	3	Relais 3	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	66	*/	{	REL3	,	2	,	0	}	,	/*	REL Module 3	Relais 3	*/
68	67	REL	3	Relais 4	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	67	*/	{	REL3	,	3	,	0	}	,	/*	REL Module 3	Relais 4	*/
69	68	REL	3	Relais 5	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	68	*/	{	REL3	,	4	,	0	}	,	/*	REL Module 3	Relais 5	*/
70	69	REL	3	Relais 6	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	69	*/	{	REL3	,	5	,	0	}	,	/*	REL Module 3	Relais 6	*/
71	70	REL	3	Relais 7	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	70	*/	{	REL3	,	6	,	0	}	,	/*	REL Module 3	Relais 7	*/
72	71	REL	3	Relais 8	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	71	*/	{	REL3	,	7	,	0	}	,	/*	REL Module 3	Relais 8	*/
73	72	REL	4	Relais 1	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	72	*/	{	REL4	,	0	,	0	}	,	/*	REL Module 4	Relais 1	*/
74	73	REL	4	Relais 2	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	73	*/	{	REL4	,	1	,	0	}	,	/*	REL Module 4	Relais 2	*/
75	74	REL	4	Relais 3	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	74	*/	{	REL4	,	2	,	0	}	,	/*	REL Module 4	Relais 3	*/
76	75	REL	4	Relais 4	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	75	*/	{	REL4	,	3	,	0	}	,	/*	REL Module 4	Relais 4	*/
77	76	REL	4	Relais 5	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	76	*/	{	REL4	,	4	,	0	}	,	/*	REL Module 4	Relais 5	*/
78	77	REL	4	Relais 6	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	77	*/	{	REL4	,	5	,	0	}	,	/*	REL Module 4	Relais 6	*/
79	78	REL	4	Relais 7	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	78	*/	{	REL4	,	6	,	0	}	,	/*	REL Module 4	Relais 7	*/
80	79	REL	4	Relais 8	0,1	Sets the Relais to on(=1) or off(=0) Status. Default status = 0		/*	79	*/	{	REL4	,	7	,	0	}	,	/*	REL Module 4	Relais 8	*/
				};

## Discrete Input Contacts
				TABLE	Module NR		MREG
Register Adress	Offset	Type	Mod.Nr.	Name	Values	Description
10001	0	LEAFLET		FAULT_OUT				/*	0	*/	{	LEAFLET	,	0	}	,	/*	LEAFLET Module	FAULT_OUT	*/
10002	1	LEAFLET		FAULT_HBUS24				/*	1	*/	{	LEAFLET	,	1	}	,	/*	LEAFLET Module	FAULT_HBUS24	*/
10003	2	LEAFLET		FAULT_HBUS				/*	2	*/	{	LEAFLET	,	2	}	,	/*	LEAFLET Module	FAULT_HBUS	*/
10004	3	LEAFLET		SWITCH IN 1				/*	3	*/	{	LEAFLET	,	3	}	,	/*	LEAFLET Module	SWITCH IN 1	*/
10005	4	LEAFLET		SWITCH IN 2				/*	4	*/	{	LEAFLET	,	4	}	,	/*	LEAFLET Module	SWITCH IN 2	*/
10006	5	LEAFLET		SWITCH IN 3				/*	5	*/	{	LEAFLET	,	5	}	,	/*	LEAFLET Module	SWITCH IN 3	*/
10007	6	LEAFLET		SWITCH IN 4				/*	6	*/	{	LEAFLET	,	6	}	,	/*	LEAFLET Module	SWITCH IN 4	*/
10008	7	LEAFLET		ISO IN 1				/*	7	*/	{	LEAFLET	,	7	}	,	/*	LEAFLET Module	ISO IN 1	*/
10009	8	LEAFLET		ISO IN 2				/*	8	*/	{	LEAFLET	,	8	}	,	/*	LEAFLET Module	ISO IN 2	*/
10010	9	LEAFLET		RESERVED				/*	9	*/	{	LEAFLET	,	9	}	,	/*	LEAFLET Module	RESERVED	*/
10011	10	LEAFLET		RESERVED				/*	10	*/	{	LEAFLET	,	10	}	,	/*	LEAFLET Module	RESERVED	*/
10012	11	LEAFLET		RESERVED				/*	11	*/	{	LEAFLET	,	11	}	,	/*	LEAFLET Module	RESERVED	*/
10013	12	LEAFLET		RESERVED				/*	12	*/	{	LEAFLET	,	12	}	,	/*	LEAFLET Module	RESERVED	*/
10014	13	LEAFLET		RESERVED				/*	13	*/	{	LEAFLET	,	13	}	,	/*	LEAFLET Module	RESERVED	*/
10015	14	LEAFLET		RESERVED				/*	14	*/	{	LEAFLET	,	14	}	,	/*	LEAFLET Module	RESERVED	*/
10016	15	LEAFLET		RESERVED				/*	15	*/	{	LEAFLET	,	15	}	,	/*	LEAFLET Module	RESERVED	*/
10017	16	AIO	1	Digital Input 1		Holds the Status of the Digital Input		/*	16	*/	{	AIO1	,	0	}	,	/*	AIO Module 1	Digital Input 1	*/
10018	17	AIO	1	Digital Input 2		Holds the Status of the Digital Input		/*	17	*/	{	AIO1	,	1	}	,	/*	AIO Module 1	Digital Input 2	*/
10019	18	AIO	1	Digital Input 3		Holds the Status of the Digital Input		/*	18	*/	{	AIO1	,	2	}	,	/*	AIO Module 1	Digital Input 3	*/
10020	19	AIO	1	Digital Input 4		Holds the Status of the Digital Input		/*	19	*/	{	AIO1	,	3	}	,	/*	AIO Module 1	Digital Input 4	*/
10021	20	AIO	2	Digital Input 1		Holds the Status of the Digital Input		/*	20	*/	{	AIO2	,	0	}	,	/*	AIO Module 2	Digital Input 1	*/
10022	21	AIO	2	Digital Input 2		Holds the Status of the Digital Input		/*	21	*/	{	AIO2	,	1	}	,	/*	AIO Module 2	Digital Input 2	*/
10023	22	AIO	2	Digital Input 3		Holds the Status of the Digital Input		/*	22	*/	{	AIO2	,	2	}	,	/*	AIO Module 2	Digital Input 3	*/
10024	23	AIO	2	Digital Input 4		Holds the Status of the Digital Input		/*	23	*/	{	AIO2	,	3	}	,	/*	AIO Module 2	Digital Input 4	*/
10025	24	AIO	3	Digital Input 1		Holds the Status of the Digital Input		/*	24	*/	{	AIO3	,	0	}	,	/*	AIO Module 3	Digital Input 1	*/
10026	25	AIO	3	Digital Input 2		Holds the Status of the Digital Input		/*	25	*/	{	AIO3	,	1	}	,	/*	AIO Module 3	Digital Input 2	*/
10027	26	AIO	3	Digital Input 3		Holds the Status of the Digital Input		/*	26	*/	{	AIO3	,	2	}	,	/*	AIO Module 3	Digital Input 3	*/
10028	27	AIO	3	Digital Input 4		Holds the Status of the Digital Input		/*	27	*/	{	AIO3	,	3	}	,	/*	AIO Module 3	Digital Input 4	*/
10029	28	AIO	4	Digital Input 1		Holds the Status of the Digital Input		/*	28	*/	{	AIO4	,	0	}	,	/*	AIO Module 4	Digital Input 1	*/
10030	29	AIO	4	Digital Input 2		Holds the Status of the Digital Input		/*	29	*/	{	AIO4	,	1	}	,	/*	AIO Module 4	Digital Input 2	*/
10031	30	AIO	4	Digital Input 3		Holds the Status of the Digital Input		/*	30	*/	{	AIO4	,	2	}	,	/*	AIO Module 4	Digital Input 3	*/
10032	31	AIO	4	Digital Input 4		Holds the Status of the Digital Input		/*	31	*/	{	AIO4	,	3	}	,	/*	AIO Module 4	Digital Input 4	*/
10033	32	AIO	5	Digital Input 1		Holds the Status of the Digital Input		/*	32	*/	{	AIO5	,	0	}	,	/*	AIO Module 5	Digital Input 1	*/
10034	33	AIO	5	Digital Input 2		Holds the Status of the Digital Input		/*	33	*/	{	AIO5	,	1	}	,	/*	AIO Module 5	Digital Input 2	*/
10035	34	AIO	5	Digital Input 3		Holds the Status of the Digital Input		/*	34	*/	{	AIO5	,	2	}	,	/*	AIO Module 5	Digital Input 3	*/
10036	35	AIO	5	Digital Input 4		Holds the Status of the Digital Input		/*	35	*/	{	AIO5	,	3	}	,	/*	AIO Module 5	Digital Input 4	*/
10037	36	AIO	6	Digital Input 1		Holds the Status of the Digital Input		/*	36	*/	{	AIO6	,	0	}	,	/*	AIO Module 6	Digital Input 1	*/
10038	37	AIO	6	Digital Input 2		Holds the Status of the Digital Input		/*	37	*/	{	AIO6	,	1	}	,	/*	AIO Module 6	Digital Input 2	*/
10039	38	AIO	6	Digital Input 3		Holds the Status of the Digital Input		/*	38	*/	{	AIO6	,	2	}	,	/*	AIO Module 6	Digital Input 3	*/
10040	39	AIO	6	Digital Input 4		Holds the Status of the Digital Input		/*	39	*/	{	AIO6	,	3	}	,	/*	AIO Module 6	Digital Input 4	*/
10041	40	AIO	7	Digital Input 1		Holds the Status of the Digital Input		/*	40	*/	{	AIO7	,	0	}	,	/*	AIO Module 7	Digital Input 1	*/
10042	41	AIO	7	Digital Input 2		Holds the Status of the Digital Input		/*	41	*/	{	AIO7	,	1	}	,	/*	AIO Module 7	Digital Input 2	*/
10043	42	AIO	7	Digital Input 3		Holds the Status of the Digital Input		/*	42	*/	{	AIO7	,	2	}	,	/*	AIO Module 7	Digital Input 3	*/
10044	43	AIO	7	Digital Input 4		Holds the Status of the Digital Input		/*	43	*/	{	AIO7	,	3	}	,	/*	AIO Module 7	Digital Input 4	*/

## Analog Input Registers
				TABLE	Module NR		MREG
Register Adress	Offset	Type	ModNR	Name	Values	Description
30001	0	LEAFLET		Errors				/*	0	*/	{	LEAFLET	,	0	}	,	/*	LEAFLET Module	Leaflet Software Version Major	*/
30002	1	LEAFLET		Leaflet Software Version Major		MAJOR		/*	1	*/	{	LEAFLET	,	1	}	,	/*	LEAFLET Module	Leaflet Software Version Minor	*/
30003	2	LEAFLET		Leaflet Software Version Minor		MINOR		/*	2	*/	{	LEAFLET	,	2	}	,	/*	LEAFLET Module	Leaflet Software Version Patch	*/
30004	3	LEAFLET		Leaflet Software Version Patch		PATCH		/*	3	*/	{	LEAFLET	,	3	}	,	/*	LEAFLET Module	PWM Modul Connection Status / Bit 0 = PWM Module 1 / Bit 1 = PWM Module 2 / Bit 2 = PWM Module 3 / Bit 3 = PWM Module 4 / Bit 4 = PWM Module 5 / Bit 5 = PWM Module 6 / Bit 6 = PWM Module 7 / Bit 7 = PWM Module 8 / …	*/
30005	4	LEAFLET		Serial Nr MSB				/*	4	*/	{	LEAFLET	,	4	}	,	/*	LEAFLET Module	REL Modul Connection Status / Bit 0 = REL Module 0 / Bit 1 = REL Module 1 / Bit 2 = REL Module 2 / Bit 3 = REL Module 3	*/
30006	5	LEAFLET		Serial Nr				/*	5	*/	{	LEAFLET	,	5	}	,	/*	LEAFLET Module	TMP Modul Connection Status / Bit 0 = TMP Module 1 / Bit 1 = TMP Module 2 / Bit 2 = TMP Module 3 / Bit 3 = TMP Module 4 / Bit 4 = TMP Module 5 / Bit 5 = TMP Module 6 / Bit 6 = TMP Module 7	*/
30007	6	LEAFLET		Serial Nr				/*	6	*/	{	LEAFLET	,	6	}	,	/*	LEAFLET Module	AIO Modul Connection Status / Bit 0 = AIO Module 1 / Bit 1 = AIO Module 2 / Bit 2 = AIO Module 3 / Bit 3 = AIO Module 4 / Bit 4 = AIO Module 5 / Bit 5 = AIO Module 6 / Bit 6 = AIO Module 7	*/
30008	7	LEAFLET		SerialNR Lsb				/*	7	*/	{	LEAFLET	,	7	}	,	/*	LEAFLET Module	REL Modul Connection Status / Bit 0 = REL Module 0 / Bit 1 = REL Module 1 / Bit 2 = REL Module 2 / Bit 3 = REL Module 3	*/
30009	8	LEAFLET		PWM Modul Connection Status / Bit 0 = PWM Module 1 / Bit 1 = PWM Module 2 / Bit 2 = PWM Module 3 / Bit 3 = PWM Module 4 / Bit 4 = PWM Module 5 / Bit 5 = PWM Module 6 / Bit 6 = PWM Module 7 / Bit 7 = PWM Module 8 / …	0=Not Connected / 1 = Connected	This Register holds Information which Pulse-width-modulation Modules have been detected.		/*	8	*/	{	LEAFLET	,	8	}	,	/*	LEAFLET Module	TMP Modul Connection Status / Bit 0 = TMP Module 1 / Bit 1 = TMP Module 2 / Bit 2 = TMP Module 3 / Bit 3 = TMP Module 4 / Bit 4 = TMP Module 5 / Bit 5 = TMP Module 6 / Bit 6 = TMP Module 7	*/
30010	9	LEAFLET		REL Modul Connection Status / Bit 0 = REL Module 0 / Bit 1 = REL Module 1 / Bit 2 = REL Module 2 / Bit 3 = REL Module 3	0=Not Connected / 1 = Connected	This Register holds Information which Relay Modules have been detected.		/*	9	*/	{	LEAFLET	,	9	}	,	/*	LEAFLET Module	AIO Modul Connection Status / Bit 0 = AIO Module 1 / Bit 1 = AIO Module 2 / Bit 2 = AIO Module 3 / Bit 3 = AIO Module 4 / Bit 4 = AIO Module 5 / Bit 5 = AIO Module 6 / Bit 6 = AIO Module 7	*/
30011	10	LEAFLET		TMP Modul Connection Status / Bit 0 = TMP Module 1 / Bit 1 = TMP Module 2 / Bit 2 = TMP Module 3 / Bit 3 = TMP Module 4 / Bit 4 = TMP Module 5 / Bit 5 = TMP Module 6 / Bit 6 = TMP Module 7	0=Not Connected / 1 = Connected	This Register holds Information which Temperature Modules have been detected.		/*	10	*/	{	LEAFLET	,	10	}	,	/*	LEAFLET Module	TMP Modul Connection Status / Bit 0 = TMP Module 1 / Bit 1 = TMP Module 2 / Bit 2 = TMP Module 3 / Bit 3 = TMP Module 4 / Bit 4 = TMP Module 5 / Bit 5 = TMP Module 6 / Bit 6 = TMP Module 7	*/
30012	11	LEAFLET		AIO Modul Connection Status / Bit 0 = AIO Module 1 / Bit 1 = AIO Module 2 / Bit 2 = AIO Module 3 / Bit 3 = AIO Module 4 / Bit 4 = AIO Module 5 / Bit 5 = AIO Module 6 / Bit 6 = AIO Module 7	0=Not Connected / 1 = Connected	This Register holds Information which Analog Input/Output Modules have been detected.		/*	11	*/	{	LEAFLET	,	11	}	,	/*	LEAFLET Module	AIO Modul Connection Status / Bit 0 = AIO Module 1 / Bit 1 = AIO Module 2 / Bit 2 = AIO Module 3 / Bit 3 = AIO Module 4 / Bit 4 = AIO Module 5 / Bit 5 = AIO Module 6 / Bit 6 = AIO Module 7	*/
30013	12	LEAFLET		RESERVED				/*	12	*/	{	LEAFLET	,	12	}	,	/*	LEAFLET Module	RESERVED	*/
30014	13	LEAFLET		RESERVED				/*	13	*/	{	LEAFLET	,	13	}	,	/*	LEAFLET Module	RESERVED	*/
30015	14	LEAFLET		RESERVED				/*	14	*/	{	LEAFLET	,	14	}	,	/*	LEAFLET Module	RESERVED	*/
30016	15	LEAFLET		RESERVED				/*	15	*/	{	LEAFLET	,	15	}	,	/*	LEAFLET Module	RESERVED	*/
30017	16	PWM	1	Errors				/*	16	*/	{	PWM1	,	0	}	,	/*	PWM Module 1	Errors	*/
30018	17	PWM	2	Errors				/*	17	*/	{	PWM2	,	0	}	,	/*	PWM Module 2	Errors	*/
30019	18	PWM	3	Errors				/*	18	*/	{	PWM3	,	0	}	,	/*	PWM Module 3	Errors	*/
30020	19	PWM	4	Errors				/*	19	*/	{	PWM4	,	0	}	,	/*	PWM Module 4	Errors	*/
30021	20	PWM	5	Errors				/*	20	*/	{	PWM5	,	0	}	,	/*	PWM Module 5	Errors	*/
30022	21	PWM	6	Errors				/*	21	*/	{	PWM6	,	0	}	,	/*	PWM Module 6	Errors	*/
30023	22	PWM	7	Errors				/*	22	*/	{	PWM7	,	0	}	,	/*	PWM Module 7	Errors	*/
30024	23	PWM	8	Errors				/*	23	*/	{	PWM8	,	0	}	,	/*	PWM Module 8	Errors	*/
30025	24	REL	1	Errors				/*	24	*/	{	REL1	,	0	}	,	/*	REL Module 1	Errors	*/
30026	25	REL	2	Errors				/*	25	*/	{	REL2	,	0	}	,	/*	REL Module 2	Errors	*/
30027	26	REL	3	Errors				/*	26	*/	{	REL3	,	0	}	,	/*	REL Module 3	Errors	*/
30028	27	REL	4	Errors				/*	27	*/	{	REL4	,	0	}	,	/*	REL Module 4	Errors	*/
30029	28	TMP	1	Errors				/*	28	*/	{	TMP1	,	0	}	,	/*	TMP Module 1	Errors	*/
30030	29	TMP	2	Errors				/*	29	*/	{	TMP2	,	0	}	,	/*	TMP Module 2	Errors	*/
30031	30	TMP	3	Errors				/*	30	*/	{	TMP3	,	0	}	,	/*	TMP Module 3	Errors	*/
30032	31	AIO	1	Error Flags		This Register holds the Error Flags of AIO Module 1		/*	31	*/	{	AIO1	,	0	}	,	/*	AIO Module 1	Error Flags	*/
30033	32	AIO	2	Error Flags		This Register holds the Error Flags of AIO Module 2		/*	32	*/	{	AIO2	,	0	}	,	/*	AIO Module 2	Error Flags	*/
30034	33	AIO	3	Error Flags		This Register holds the Error Flags of AIO Module 3		/*	33	*/	{	AIO3	,	0	}	,	/*	AIO Module 3	Error Flags	*/
30035	34	AIO	4	Error Flags		This Register holds the Error Flags of AIO Module 4		/*	34	*/	{	AIO4	,	0	}	,	/*	AIO Module 4	Error Flags	*/
30036	35	AIO	5	Error Flags		This Register holds the Error Flags of AIO Module 5		/*	35	*/	{	AIO5	,	0	}	,	/*	AIO Module 5	Error Flags	*/
30037	36	AIO	6	Error Flags		This Register holds the Error Flags of AIO Module 6		/*	36	*/	{	AIO6	,	0	}	,	/*	AIO Module 6	Error Flags	*/
30038	37	AIO	7	Error Flags		This Register holds the Error Flags of AIO Module 7		/*	37	*/	{	AIO7	,	0	}	,	/*	AIO Module 7	Error Flags	*/
30039	38	TMP	1	Temperature 1	-40.8°C to 1128 °C	This Temperature is encoded as signed short in deziDegree for precission.		/*	38	*/	{	TMP1	,	1	}	,	/*	TMP Module 1	Temperature 1	*/
30040	39	TMP	1	Temperature 2	-40.8°C to 1128 °C	as above		/*	39	*/	{	TMP1	,	2	}	,	/*	TMP Module 1	Temperature 2	*/
30041	40	TMP	1	Temperature 3	-40.8°C to 1128 °C	as above		/*	40	*/	{	TMP1	,	3	}	,	/*	TMP Module 1	Temperature 3	*/
30042	41	TMP	1	Temperature 4	-40.8°C to 1128 °C	as above		/*	41	*/	{	TMP1	,	4	}	,	/*	TMP Module 1	Temperature 4	*/
30043	42	TMP	1	Temperature 5	-40.8°C to 1128 °C	as above		/*	42	*/	{	TMP1	,	5	}	,	/*	TMP Module 1	Temperature 5	*/
30044	43	TMP	1	Temperature 6	-40.8°C to 1128 °C	as above		/*	43	*/	{	TMP1	,	6	}	,	/*	TMP Module 1	Temperature 6	*/
30045	44	TMP	1	Temperature 7	-40.8°C to 1128 °C	as above		/*	44	*/	{	TMP1	,	7	}	,	/*	TMP Module 1	Temperature 7	*/
30046	45	TMP	1	Temperature 8	-40.8°C to 1128 °C	as above		/*	45	*/	{	TMP1	,	8	}	,	/*	TMP Module 1	Temperature 8	*/
30047	46	TMP	1	Temperature 9	-40.8°C to 1128 °C	as above		/*	46	*/	{	TMP1	,	9	}	,	/*	TMP Module 1	Temperature 9	*/
30048	47	TMP	1	Temperature 10	-40.8°C to 1128 °C	as above		/*	47	*/	{	TMP1	,	10	}	,	/*	TMP Module 1	Temperature 10	*/
30049	48	TMP	1	Temperature 11	-40.8°C to 1128 °C	as above		/*	48	*/	{	TMP1	,	11	}	,	/*	TMP Module 1	Temperature 11	*/
30050	49	TMP	1	Temperature 12	-40.8°C to 1128 °C	as above		/*	49	*/	{	TMP1	,	12	}	,	/*	TMP Module 1	Temperature 12	*/
30051	50	TMP	1	Temperature 13	-40.8°C to 1128 °C	as above		/*	50	*/	{	TMP1	,	13	}	,	/*	TMP Module 1	Temperature 13	*/
30052	51	TMP	1	Temperature 14	-40.8°C to 1128 °C	as above		/*	51	*/	{	TMP1	,	14	}	,	/*	TMP Module 1	Temperature 14	*/
30053	52	TMP	1	Temperature 15	-40.8°C to 1128 °C	as above		/*	52	*/	{	TMP1	,	15	}	,	/*	TMP Module 1	Temperature 15	*/
30054	53	TMP	1	Temperature 16	-40.8°C to 1128 °C	as above		/*	53	*/	{	TMP1	,	16	}	,	/*	TMP Module 1	Temperature 16	*/
30055	54	TMP	2	Temperature 1	-40.8°C to 1128 °C	as above		/*	54	*/	{	TMP2	,	1	}	,	/*	TMP Module 2	Temperature 1	*/
30056	55	TMP	2	Temperature 2	-40.8°C to 1128 °C	as above		/*	55	*/	{	TMP2	,	2	}	,	/*	TMP Module 2	Temperature 2	*/
30057	56	TMP	2	Temperature 3	-40.8°C to 1128 °C	as above		/*	56	*/	{	TMP2	,	3	}	,	/*	TMP Module 2	Temperature 3	*/
30058	57	TMP	2	Temperature 4	-40.8°C to 1128 °C	as above		/*	57	*/	{	TMP2	,	4	}	,	/*	TMP Module 2	Temperature 4	*/
30059	58	TMP	2	Temperature 5	-40.8°C to 1128 °C	as above		/*	58	*/	{	TMP2	,	5	}	,	/*	TMP Module 2	Temperature 5	*/
30060	59	TMP	2	Temperature 6	-40.8°C to 1128 °C	as above		/*	59	*/	{	TMP2	,	6	}	,	/*	TMP Module 2	Temperature 6	*/
30061	60	TMP	2	Temperature 7	-40.8°C to 1128 °C	as above		/*	60	*/	{	TMP2	,	7	}	,	/*	TMP Module 2	Temperature 7	*/
30062	61	TMP	2	Temperature 8	-40.8°C to 1128 °C	as above		/*	61	*/	{	TMP2	,	8	}	,	/*	TMP Module 2	Temperature 8	*/
30063	62	TMP	2	Temperature 9	-40.8°C to 1128 °C	as above		/*	62	*/	{	TMP2	,	9	}	,	/*	TMP Module 2	Temperature 9	*/
30064	63	TMP	2	Temperature 10	-40.8°C to 1128 °C	as above		/*	63	*/	{	TMP2	,	10	}	,	/*	TMP Module 2	Temperature 10	*/
30065	64	TMP	2	Temperature 11	-40.8°C to 1128 °C	as above		/*	64	*/	{	TMP2	,	11	}	,	/*	TMP Module 2	Temperature 11	*/
30066	65	TMP	2	Temperature 12	-40.8°C to 1128 °C	as above		/*	65	*/	{	TMP2	,	12	}	,	/*	TMP Module 2	Temperature 12	*/
30067	66	TMP	2	Temperature 13	-40.8°C to 1128 °C	as above		/*	66	*/	{	TMP2	,	13	}	,	/*	TMP Module 2	Temperature 13	*/
30068	67	TMP	2	Temperature 14	-40.8°C to 1128 °C	as above		/*	67	*/	{	TMP2	,	14	}	,	/*	TMP Module 2	Temperature 14	*/
30069	68	TMP	2	Temperature 15	-40.8°C to 1128 °C	as above		/*	68	*/	{	TMP2	,	15	}	,	/*	TMP Module 2	Temperature 15	*/
30070	69	TMP	2	Temperature 16	-40.8°C to 1128 °C	as above		/*	69	*/	{	TMP2	,	16	}	,	/*	TMP Module 2	Temperature 16	*/
30071	70	TMP	3	Temperature 1	-40.8°C to 1128 °C	as above		/*	70	*/	{	TMP3	,	1	}	,	/*	TMP Module 3	Temperature 1	*/
30072	71	TMP	3	Temperature 2	-40.8°C to 1128 °C	as above		/*	71	*/	{	TMP3	,	2	}	,	/*	TMP Module 3	Temperature 2	*/
30073	72	TMP	3	Temperature 3	-40.8°C to 1128 °C	as above		/*	72	*/	{	TMP3	,	3	}	,	/*	TMP Module 3	Temperature 3	*/
30074	73	TMP	3	Temperature 4	-40.8°C to 1128 °C	as above		/*	73	*/	{	TMP3	,	4	}	,	/*	TMP Module 3	Temperature 4	*/
30075	74	TMP	3	Temperature 5	-40.8°C to 1128 °C	as above		/*	74	*/	{	TMP3	,	5	}	,	/*	TMP Module 3	Temperature 5	*/
30076	75	TMP	3	Temperature 6	-40.8°C to 1128 °C	as above		/*	75	*/	{	TMP3	,	6	}	,	/*	TMP Module 3	Temperature 6	*/
30077	76	TMP	3	Temperature 7	-40.8°C to 1128 °C	as above		/*	76	*/	{	TMP3	,	7	}	,	/*	TMP Module 3	Temperature 7	*/
30078	77	TMP	3	Temperature 8	-40.8°C to 1128 °C	as above		/*	77	*/	{	TMP3	,	8	}	,	/*	TMP Module 3	Temperature 8	*/
30079	78	TMP	3	Temperature 9	-40.8°C to 1128 °C	as above		/*	78	*/	{	TMP3	,	9	}	,	/*	TMP Module 3	Temperature 9	*/
30080	79	TMP	3	Temperature 10	-40.8°C to 1128 °C	as above		/*	79	*/	{	TMP3	,	10	}	,	/*	TMP Module 3	Temperature 10	*/
30081	80	TMP	3	Temperature 11	-40.8°C to 1128 °C	as above		/*	80	*/	{	TMP3	,	11	}	,	/*	TMP Module 3	Temperature 11	*/
30082	81	TMP	3	Temperature 12	-40.8°C to 1128 °C	as above		/*	81	*/	{	TMP3	,	12	}	,	/*	TMP Module 3	Temperature 12	*/
30083	82	TMP	3	Temperature 13	-40.8°C to 1128 °C	as above		/*	82	*/	{	TMP3	,	13	}	,	/*	TMP Module 3	Temperature 13	*/
30084	83	TMP	3	Temperature 14	-40.8°C to 1128 °C	as above		/*	83	*/	{	TMP3	,	14	}	,	/*	TMP Module 3	Temperature 14	*/
30085	84	TMP	3	Temperature 15	-40.8°C to 1128 °C	as above		/*	84	*/	{	TMP3	,	15	}	,	/*	TMP Module 3	Temperature 15	*/
30086	85	TMP	3	Temperature 16	-40.8°C to 1128 °C	as above		/*	85	*/	{	TMP3	,	16	}	,	/*	TMP Module 3	Temperature 16	*/
30087	86	AIO	1	Temp 1		Encoded somehow		/*	86	*/	{	AIO1	,	5	}	,	/*	AIO Module 1	Temp 1	*/
30088	87	AIO	1	Temp 2				/*	87	*/	{	AIO1	,	6	}	,	/*	AIO Module 1	Temp 2	*/
30089	88	AIO	1	Temp 3				/*	88	*/	{	AIO1	,	7	}	,	/*	AIO Module 1	Temp 3	*/
30090	89	AIO	1	Temp 4				/*	89	*/	{	AIO1	,	8	}	,	/*	AIO Module 1	Temp 4	*/
30091	90	AIO	2	Temp 1				/*	90	*/	{	AIO2	,	5	}	,	/*	AIO Module 2	Temp 1	*/
30092	91	AIO	2	Temp 2				/*	91	*/	{	AIO2	,	6	}	,	/*	AIO Module 2	Temp 2	*/
30093	92	AIO	2	Temp 3				/*	92	*/	{	AIO2	,	7	}	,	/*	AIO Module 2	Temp 3	*/
30094	93	AIO	2	Temp 4				/*	93	*/	{	AIO2	,	8	}	,	/*	AIO Module 2	Temp 4	*/
30095	94	AIO	3	Temp 1				/*	94	*/	{	AIO3	,	5	}	,	/*	AIO Module 3	Temp 1	*/
30096	95	AIO	3	Temp 2				/*	95	*/	{	AIO3	,	6	}	,	/*	AIO Module 3	Temp 2	*/
30097	96	AIO	3	Temp 3				/*	96	*/	{	AIO3	,	7	}	,	/*	AIO Module 3	Temp 3	*/
30098	97	AIO	3	Temp 4				/*	97	*/	{	AIO3	,	8	}	,	/*	AIO Module 3	Temp 4	*/
30099	98	AIO	4	Temp 1				/*	98	*/	{	AIO4	,	5	}	,	/*	AIO Module 4	Temp 1	*/
30100	99	AIO	4	Temp 2				/*	99	*/	{	AIO4	,	6	}	,	/*	AIO Module 4	Temp 2	*/
30101	100	AIO	4	Temp 3				/*	100	*/	{	AIO4	,	7	}	,	/*	AIO Module 4	Temp 3	*/
30102	101	AIO	4	Temp 4				/*	101	*/	{	AIO4	,	8	}	,	/*	AIO Module 4	Temp 4	*/
30103	102	AIO	5	Temp 1				/*	102	*/	{	AIO5	,	5	}	,	/*	AIO Module 5	Temp 1	*/
30104	103	AIO	5	Temp 2				/*	103	*/	{	AIO5	,	6	}	,	/*	AIO Module 5	Temp 2	*/
30105	104	AIO	5	Temp 3				/*	104	*/	{	AIO5	,	7	}	,	/*	AIO Module 5	Temp 3	*/
30106	105	AIO	5	Temp 4				/*	105	*/	{	AIO5	,	8	}	,	/*	AIO Module 5	Temp 4	*/
30107	106	AIO	6	Temp 1				/*	106	*/	{	AIO6	,	5	}	,	/*	AIO Module 6	Temp 1	*/
30108	107	AIO	6	Temp 2				/*	107	*/	{	AIO6	,	6	}	,	/*	AIO Module 6	Temp 2	*/
30109	108	AIO	6	Temp 3				/*	108	*/	{	AIO6	,	7	}	,	/*	AIO Module 6	Temp 3	*/
30110	109	AIO	6	Temp 4				/*	109	*/	{	AIO6	,	8	}	,	/*	AIO Module 6	Temp 4	*/
30111	110	AIO	7	Temp 1				/*	110	*/	{	AIO7	,	5	}	,	/*	AIO Module 7	Temp 1	*/
30112	111	AIO	7	Temp 2				/*	111	*/	{	AIO7	,	6	}	,	/*	AIO Module 7	Temp 2	*/
30113	112	AIO	7	Temp 3				/*	112	*/	{	AIO7	,	7	}	,	/*	AIO Module 7	Temp 3	*/
30114	113	AIO	7	Temp 4				/*	113	*/	{	AIO7	,	8	}	,	/*	AIO Module 7	Temp 4	*/
30115	114	AIO	1	Pecentual Input 1	0.0-100.0%	Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 1 Config (ADRESS). / For presission Values are multiplied by ten. 100% = 1000.		/*	114	*/	{	AIO1	,	1	}	,	/*	AIO Module 1	Pecentual Input 1	*/
30116	115	AIO	1	Pecentual Input 2	0.0-100.0%	as above		/*	115	*/	{	AIO1	,	2	}	,	/*	AIO Module 1	Pecentual Input 2	*/
30117	116	AIO	1	Pecentual Input 3	0.0-100.0%	as above		/*	116	*/	{	AIO1	,	3	}	,	/*	AIO Module 1	Pecentual Input 3	*/
30118	117	AIO	1	Pecentual Input 4	0.0-100.0%	as above		/*	117	*/	{	AIO1	,	4	}	,	/*	AIO Module 1	Pecentual Input 4	*/
30119	118	AIO	2	Pecentual Input 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 2 Config (ADRESS). / The Readback value has to be devided by 10.		/*	118	*/	{	AIO2	,	1	}	,	/*	AIO Module 2	Pecentual Input 1	*/
30120	119	AIO	2	Pecentual Input 2	0.0-100.0%	as above		/*	119	*/	{	AIO2	,	2	}	,	/*	AIO Module 2	Pecentual Input 2	*/
30121	120	AIO	2	Pecentual Input 3	0.0-100.0%	as above		/*	120	*/	{	AIO2	,	3	}	,	/*	AIO Module 2	Pecentual Input 3	*/
30122	121	AIO	2	Pecentual Input 4	0.0-100.0%	as above		/*	121	*/	{	AIO2	,	4	}	,	/*	AIO Module 2	Pecentual Input 4	*/
30123	122	AIO	3	Pecentual Input 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 3 Config (ADRESS). / The Readback value has to be devided by 10.		/*	122	*/	{	AIO3	,	1	}	,	/*	AIO Module 3	Pecentual Input 1	*/
30124	123	AIO	3	Pecentual Input 2	0.0-100.0%	as above		/*	123	*/	{	AIO3	,	2	}	,	/*	AIO Module 3	Pecentual Input 2	*/
30125	124	AIO	3	Pecentual Input 3	0.0-100.0%	as above		/*	124	*/	{	AIO3	,	3	}	,	/*	AIO Module 3	Pecentual Input 3	*/
30126	125	AIO	3	Pecentual Input 4	0.0-100.0%	as above		/*	125	*/	{	AIO3	,	4	}	,	/*	AIO Module 3	Pecentual Input 4	*/
30127	126	AIO	4	Pecentual Input 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 4 Config (ADRESS). / The Readback value has to be devided by 10.		/*	126	*/	{	AIO4	,	1	}	,	/*	AIO Module 4	Pecentual Input 1	*/
30128	127	AIO	4	Pecentual Input 2	0.0-100.0%	as above		/*	127	*/	{	AIO4	,	2	}	,	/*	AIO Module 4	Pecentual Input 2	*/
30129	128	AIO	4	Pecentual Input 3	0.0-100.0%	as above		/*	128	*/	{	AIO4	,	3	}	,	/*	AIO Module 4	Pecentual Input 3	*/
30130	129	AIO	4	Pecentual Input 4	0.0-100.0%	as above		/*	129	*/	{	AIO4	,	4	}	,	/*	AIO Module 4	Pecentual Input 4	*/
30131	130	AIO	5	Pecentual Input 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 5 Config (ADRESS). / The Readback value has to be devided by 10.		/*	130	*/	{	AIO5	,	1	}	,	/*	AIO Module 5	Pecentual Input 1	*/
30132	131	AIO	5	Pecentual Input 2	0.0-100.0%	as above		/*	131	*/	{	AIO5	,	2	}	,	/*	AIO Module 5	Pecentual Input 2	*/
30133	132	AIO	5	Pecentual Input 3	0.0-100.0%	as above		/*	132	*/	{	AIO5	,	3	}	,	/*	AIO Module 5	Pecentual Input 3	*/
30134	133	AIO	5	Pecentual Input 4	0.0-100.0%	as above		/*	133	*/	{	AIO5	,	4	}	,	/*	AIO Module 5	Pecentual Input 4	*/
30135	134	AIO	6	Pecentual Input 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 6 Config (ADRESS). / The Readback value has to be devided by 10.		/*	134	*/	{	AIO6	,	1	}	,	/*	AIO Module 6	Pecentual Input 1	*/
30136	135	AIO	6	Pecentual Input 2	0.0-100.0%	as above		/*	135	*/	{	AIO6	,	2	}	,	/*	AIO Module 6	Pecentual Input 2	*/
30137	136	AIO	6	Pecentual Input 3	0.0-100.0%	as above		/*	136	*/	{	AIO6	,	3	}	,	/*	AIO Module 6	Pecentual Input 3	*/
30138	137	AIO	6	Pecentual Input 4	0.0-100.0%	as above		/*	137	*/	{	AIO6	,	4	}	,	/*	AIO Module 6	Pecentual Input 4	*/
30139	138	AIO	7	Pecentual Input 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 7 Config (ADRESS). / The Readback value has to be devided by 10.		/*	138	*/	{	AIO7	,	1	}	,	/*	AIO Module 7	Pecentual Input 1	*/
30140	139	AIO	7	Pecentual Input 2	0.0-100.0%	as above		/*	139	*/	{	AIO7	,	2	}	,	/*	AIO Module 7	Pecentual Input 2	*/
30141	140	AIO	7	Pecentual Input 3	0.0-100.0%	as above		/*	140	*/	{	AIO7	,	3	}	,	/*	AIO Module 7	Pecentual Input 3	*/
30142	141	AIO	7	Pecentual Input 4	0.0-100.0%	as above		/*	141	*/	{	AIO7	,	4	}	,	/*	AIO Module 7	Pecentual Input 4	*/
30143	142	AIO	1	Voltage Input 1	0-10.000 mV	This is the Voltage in millivolt measured on AIO Modul 1.		/*	142	*/	{	AIO1	,	9	}	,	/*	AIO Module 1	Voltage Input 1	*/
30144	143	AIO	1	Voltage Input 2	0-10.000 mV	as above		/*	143	*/	{	AIO1	,	10	}	,	/*	AIO Module 1	Voltage Input 2	*/
30145	144	AIO	1	Voltage Input 3	0-10.000 mV	as above		/*	144	*/	{	AIO1	,	11	}	,	/*	AIO Module 1	Voltage Input 3	*/
30146	145	AIO	1	Voltage Input 4	0-10.000 mV	as above		/*	145	*/	{	AIO1	,	12	}	,	/*	AIO Module 1	Voltage Input 4	*/
30147	146	AIO	2	Voltage Input 1	0-10.000 mV	This is the Voltage in millivolt measured on AIO Modul 2.		/*	146	*/	{	AIO2	,	9	}	,	/*	AIO Module 2	Voltage Input 1	*/
30148	147	AIO	2	Voltage Input 2	0-10.000 mV	as above		/*	147	*/	{	AIO2	,	10	}	,	/*	AIO Module 2	Voltage Input 2	*/
30149	148	AIO	2	Voltage Input 3	0-10.000 mV	as above		/*	148	*/	{	AIO2	,	11	}	,	/*	AIO Module 2	Voltage Input 3	*/
30150	149	AIO	2	Voltage Input 4	0-10.000 mV	as above		/*	149	*/	{	AIO2	,	12	}	,	/*	AIO Module 2	Voltage Input 4	*/
30151	150	AIO	3	Voltage Input 1	0-10.000 mV	This is the Voltage in millivolt measured on AIO Modul 3.		/*	150	*/	{	AIO3	,	9	}	,	/*	AIO Module 3	Voltage Input 1	*/
30152	151	AIO	3	Voltage Input 2	0-10.000 mV	as above		/*	151	*/	{	AIO3	,	10	}	,	/*	AIO Module 3	Voltage Input 2	*/
30153	152	AIO	3	Voltage Input 3	0-10.000 mV	as above		/*	152	*/	{	AIO3	,	11	}	,	/*	AIO Module 3	Voltage Input 3	*/
30154	153	AIO	3	Voltage Input 4	0-10.000 mV	as above		/*	153	*/	{	AIO3	,	12	}	,	/*	AIO Module 3	Voltage Input 4	*/
30155	154	AIO	4	Voltage Input 1	0-10.000 mV	This is the Voltage in millivolt measured on AIO Modul 4.		/*	154	*/	{	AIO4	,	9	}	,	/*	AIO Module 4	Voltage Input 1	*/
30156	155	AIO	4	Voltage Input 2	0-10.000 mV	as above		/*	155	*/	{	AIO4	,	10	}	,	/*	AIO Module 4	Voltage Input 2	*/
30157	156	AIO	4	Voltage Input 3	0-10.000 mV	as above		/*	156	*/	{	AIO4	,	11	}	,	/*	AIO Module 4	Voltage Input 3	*/
30158	157	AIO	4	Voltage Input 4	0-10.000 mV	as above		/*	157	*/	{	AIO4	,	12	}	,	/*	AIO Module 4	Voltage Input 4	*/
30159	158	AIO	5	Voltage Input 1	0-10.000 mV	This is the Voltage in millivolt measured on AIO Modul 5.		/*	158	*/	{	AIO5	,	9	}	,	/*	AIO Module 5	Voltage Input 1	*/
30160	159	AIO	5	Voltage Input 2	0-10.000 mV	as above		/*	159	*/	{	AIO5	,	10	}	,	/*	AIO Module 5	Voltage Input 2	*/
30161	160	AIO	5	Voltage Input 3	0-10.000 mV	as above		/*	160	*/	{	AIO5	,	11	}	,	/*	AIO Module 5	Voltage Input 3	*/
30162	161	AIO	5	Voltage Input 4	0-10.000 mV	as above		/*	161	*/	{	AIO5	,	12	}	,	/*	AIO Module 5	Voltage Input 4	*/
30163	162	AIO	6	Voltage Input 1	0-10.000 mV	This is the Voltage in millivolt measured on AIO Modul 6.		/*	162	*/	{	AIO6	,	9	}	,	/*	AIO Module 6	Voltage Input 1	*/
30164	163	AIO	6	Voltage Input 2	0-10.000 mV	as above		/*	163	*/	{	AIO6	,	10	}	,	/*	AIO Module 6	Voltage Input 2	*/
30165	164	AIO	6	Voltage Input 3	0-10.000 mV	as above		/*	164	*/	{	AIO6	,	11	}	,	/*	AIO Module 6	Voltage Input 3	*/
30166	165	AIO	6	Voltage Input 4	0-10.000 mV	as above		/*	165	*/	{	AIO6	,	12	}	,	/*	AIO Module 6	Voltage Input 4	*/
30167	166	AIO	7	Voltage Input 1	0-10.000 mV	This is the Voltage in millivolt measured on AIO Modul 7.		/*	166	*/	{	AIO7	,	9	}	,	/*	AIO Module 7	Voltage Input 1	*/
30168	167	AIO	7	Voltage Input 2	0-10.000 mV	as above		/*	167	*/	{	AIO7	,	10	}	,	/*	AIO Module 7	Voltage Input 2	*/
30169	168	AIO	7	Voltage Input 3	0-10.000 mV	as above		/*	168	*/	{	AIO7	,	11	}	,	/*	AIO Module 7	Voltage Input 3	*/
30170	169	AIO	7	Voltage Input 4	0-10.000 mV	as above		/*	169	*/	{	AIO7	,	12	}	,	/*	AIO Module 7	Voltage Input 4	*/
30171	170	AIO	1	Current Input 1	0-20000 mA	This is the Current in milli Ampere measured on AIO Modul 1.		/*	170	*/	{	AIO1	,	13	}	,	/*	AIO Module 1	Current Input 1	*/
30172	171	AIO	1	Current Input 2	0-20000 mA	as above		/*	171	*/	{	AIO1	,	14	}	,	/*	AIO Module 1	Current Input 2	*/
30173	172	AIO	1	Current Input 3	0-20000 mA	as above		/*	172	*/	{	AIO1	,	15	}	,	/*	AIO Module 1	Current Input 3	*/
30174	173	AIO	1	Current Input 4	0-20000 mA	as above		/*	173	*/	{	AIO1	,	16	}	,	/*	AIO Module 1	Current Input 4	*/
30175	174	AIO	2	Current Input 1	0-20000 mA	This is the Current in milli Ampere measured on AIO Modul 2.		/*	174	*/	{	AIO2	,	13	}	,	/*	AIO Module 2	Current Input 1	*/
30176	175	AIO	2	Current Input 2	0-20000 mA	as above		/*	175	*/	{	AIO2	,	14	}	,	/*	AIO Module 2	Current Input 2	*/
30177	176	AIO	2	Current Input 3	0-20000 mA	as above		/*	176	*/	{	AIO2	,	15	}	,	/*	AIO Module 2	Current Input 3	*/
30178	177	AIO	2	Current Input 4	0-20000 mA	as above		/*	177	*/	{	AIO2	,	16	}	,	/*	AIO Module 2	Current Input 4	*/
30179	178	AIO	3	Current Input 1	0-20000 mA	This is the Current in milli Ampere measured on AIO Modul 3.		/*	178	*/	{	AIO3	,	13	}	,	/*	AIO Module 3	Current Input 1	*/
30180	179	AIO	3	Current Input 2	0-20000 mA	as above		/*	179	*/	{	AIO3	,	14	}	,	/*	AIO Module 3	Current Input 2	*/
30181	180	AIO	3	Current Input 3	0-20000 mA	as above		/*	180	*/	{	AIO3	,	15	}	,	/*	AIO Module 3	Current Input 3	*/
30182	181	AIO	3	Current Input 4	0-20000 mA	as above		/*	181	*/	{	AIO3	,	16	}	,	/*	AIO Module 3	Current Input 4	*/
30183	182	AIO	4	Current Input 1	0-20000 mA	This is the Current in milli Ampere measured on AIO Modul 4.		/*	182	*/	{	AIO4	,	13	}	,	/*	AIO Module 4	Current Input 1	*/
30184	183	AIO	4	Current Input 2	0-20000 mA	as above		/*	183	*/	{	AIO4	,	14	}	,	/*	AIO Module 4	Current Input 2	*/
30185	184	AIO	4	Current Input 3	0-20000 mA	as above		/*	184	*/	{	AIO4	,	15	}	,	/*	AIO Module 4	Current Input 3	*/
30186	185	AIO	4	Current Input 4	0-20000 mA	as above		/*	185	*/	{	AIO4	,	16	}	,	/*	AIO Module 4	Current Input 4	*/
30187	186	AIO	5	Current Input 1	0-20000 mA	This is the Current in milli Ampere measured on AIO Modul 5.		/*	186	*/	{	AIO5	,	13	}	,	/*	AIO Module 5	Current Input 1	*/
30188	187	AIO	5	Current Input 2	0-20000 mA	as above		/*	187	*/	{	AIO5	,	14	}	,	/*	AIO Module 5	Current Input 2	*/
30189	188	AIO	5	Current Input 3	0-20000 mA	as above		/*	188	*/	{	AIO5	,	15	}	,	/*	AIO Module 5	Current Input 3	*/
30190	189	AIO	5	Current Input 4	0-20000 mA	as above		/*	189	*/	{	AIO5	,	16	}	,	/*	AIO Module 5	Current Input 4	*/
30191	190	AIO	6	Current Input 1	0-20000 mA	This is the Current in milli Ampere measured on AIO Modul 6.		/*	190	*/	{	AIO6	,	13	}	,	/*	AIO Module 6	Current Input 1	*/
30192	191	AIO	6	Current Input 2	0-20000 mA	as above		/*	191	*/	{	AIO6	,	14	}	,	/*	AIO Module 6	Current Input 2	*/
30193	192	AIO	6	Current Input 3	0-20000 mA	as above		/*	192	*/	{	AIO6	,	15	}	,	/*	AIO Module 6	Current Input 3	*/
30194	193	AIO	6	Current Input 4	0-20000 mA	as above		/*	193	*/	{	AIO6	,	16	}	,	/*	AIO Module 6	Current Input 4	*/
30195	194	AIO	7	Current Input 1	0-20000 mA	This is the Current in milli Ampere measured on AIO Modul 7.		/*	194	*/	{	AIO7	,	13	}	,	/*	AIO Module 7	Current Input 1	*/
30196	195	AIO	7	Current Input 2	0-20000 mA	as above		/*	195	*/	{	AIO7	,	14	}	,	/*	AIO Module 7	Current Input 2	*/
30197	196	AIO	7	Current Input 3	0-20000 mA	as above		/*	196	*/	{	AIO7	,	15	}	,	/*	AIO Module 7	Current Input 3	*/
30198	197	AIO	7	Current Input 4	0-20000 mA	as above	c	/*	197	*/	{	AIO7	,	16	}	,	/*	AIO Module 7	Current Input 4	*/

## Analog Output Holding Registers
				const __uint16_t MM_OutputRegister_Map[][3] = {
Register Adress	Offset	Type	Mod. Nr	Registername	Values	Description			/*				Module		Mreg		Lock?			*/
40001	0	LEAFLET		Command Register	1337.7331				/*	0	*/	{	LEAFLET	,	0	,	1	}	,	/*	LEAFLET0 Module Command Register	1337.7331	*/
40002	1	LEAFLET		ClientWarn/Error	[0:1] = Warning Level (0-3) / [2:3] = Error Level (0-3)	Sets the status for LEDS. To make all leds blink for example write: / 0x31 = 1 level Warning 3 level error			/*	1	*/	{	LEAFLET	,	1	,	1	}	,	/*	LEAFLET1 Module ClientWarn/Error	1	*/
40003	2	LEAFLET		RESERVED					/*	2	*/	{	LEAFLET	,	2	,	1	}	,	/*	LEAFLET2 Module RESERVED	2	*/
40004	3	LEAFLET		RESERVED					/*	3	*/	{	LEAFLET	,	3	,	1	}	,	/*	LEAFLET3 Module RESERVED	3	*/
40005	4	LEAFLET		RESERVED					/*	4	*/	{	LEAFLET	,	4	,	1	}	,	/*	LEAFLET4 Module RESERVED	4	*/
40006	5	LEAFLET		RESERVED					/*	5	*/	{	LEAFLET	,	5	,	1	}	,	/*	LEAFLET5 Module RESERVED	5	*/
40007	6	LEAFLET		RESERVED					/*	6	*/	{	LEAFLET	,	6	,	1	}	,	/*	LEAFLET6 Module RESERVED	6	*/
40008	7	LEAFLET		RESERVED					/*	7	*/	{	LEAFLET	,	7	,	1	}	,	/*	LEAFLET7 Module RESERVED	7	*/
40009	8	LEAFLET		RESERVED					/*	8	*/	{	LEAFLET	,	8	,	1	}	,	/*	LEAFLET8 Module RESERVED	8	*/
40010	9	LEAFLET		RESERVED					/*	9	*/	{	LEAFLET	,	9	,	1	}	,	/*	LEAFLET9 Module RESERVED	9	*/
40011	10	LEAFLET		RESERVED					/*	10	*/	{	LEAFLET	,	10	,	1	}	,	/*	LEAFLET10 Module RESERVED	10	*/
40012	11	LEAFLET		RESERVED					/*	11	*/	{	LEAFLET	,	11	,	1	}	,	/*	LEAFLET11 Module RESERVED	5	*/
40013	12	LEAFLET		RESERVED					/*	12	*/	{	LEAFLET	,	12	,	1	}	,	/*	LEAFLET12 Module RESERVED	6	*/
40014	13	LEAFLET		RESERVED					/*	13	*/	{	LEAFLET	,	13	,	1	}	,	/*	LEAFLET13 Module RESERVED	7	*/
40015	14	LEAFLET		RESERVED					/*	14	*/	{	LEAFLET	,	14	,	1	}	,	/*	LEAFLET14 Module RESERVED	8	*/
40016	15	LEAFLET		RESERVED					/*	15	*/	{	LEAFLET	,	15	,	1	}	,	/*	LEAFLET15 Module RESERVED	9	*/
40017	16	AIO	1	Config Register	Functions: / 0=NotUsed / 1=0-10V OUT / 2=0-10V IN / 3=0-20mA OUT / 4=0-20mA IN / 5=4-20mA OUT / 6=4-20mA IN / 7=Temp IN / 8=Digital IN	This Register is used to set the Channel Functions of the AIO Module 1. / This Register can only be written to if the Leaflet is in Configuration Mode. / Bit [3:0] =Function of Channel A / Bit [7:4] =Function of Channel B / Bit [11:8] =Function of Channel C / Bit [15:12] =Function of Channel D			/*	16	*/	{	AIO1	,	0	,	1	}	,	/*	AIO1 Module Config Register	Functions: / 0=NotUsed / 1=0-10V OUT / 2=0-10V IN / 3=0-20mA OUT / 4=0-20mA IN / 5=4-20mA OUT / 6=4-20mA IN / 7=Temp IN / 8=Digital IN	*/
40018	17	AIO	2	Config Register		This Register is used to set the Channel Functions of the AIO Module 1. / This Register can only be written to if the Leaflet is in Configuration Mode. / If configuration is accepted Readback will hold the current Config Setting. Otherwise it will be Reset to 0.			/*	17	*/	{	AIO2	,	0	,	1	}	,	/*	AIO2 Module Config Register	0	*/
40019	18	AIO	3	Config Register		This Register is used to set the Channel Functions of the AIO Module 1. / This Register can only be written to if the Leaflet is in Configuration Mode. / If configuration is accepted Readback will hold the current Config Setting. Otherwise it will be Reset to 0.			/*	18	*/	{	AIO3	,	0	,	1	}	,	/*	AIO3 Module Config Register	0	*/
40020	19	AIO	4	Config Register		This Register is used to set the Channel Functions of the AIO Module 1. / This Register can only be written to if the Leaflet is in Configuration Mode. / If configuration is accepted Readback will hold the current Config Setting. Otherwise it will be Reset to 0.			/*	19	*/	{	AIO4	,	0	,	1	}	,	/*	AIO4 Module Config Register	0	*/
40021	20	AIO	5	Config Register		This Register is used to set the Channel Functions of the AIO Module 1. / This Register can only be written to if the Leaflet is in Configuration Mode. / If configuration is accepted Readback will hold the current Config Setting. Otherwise it will be Reset to 0.			/*	20	*/	{	AIO5	,	0	,	1	}	,	/*	AIO5 Module Config Register	0	*/
40022	21	AIO	6	Config Register		This Register is used to set the Channel Functions of the AIO Module 1. / This Register can only be written to if the Leaflet is in Configuration Mode. / If configuration is accepted Readback will hold the current Config Setting. Otherwise it will be Reset to 0.			/*	21	*/	{	AIO6	,	0	,	1	}	,	/*	AIO6 Module Config Register	0	*/
40023	22	AIO	7	Config Register		This Register is used to set the Channel Functions of the AIO Module 1. / This Register can only be written to if the Leaflet is in Configuration Mode. / If configuration is accepted Readback will hold the current Config Setting. Otherwise it will be Reset to 0.			/*	22	*/	{	AIO7	,	0	,	1	}	,	/*	AIO7 Module Config Register	0	*/
40024	23	REL	1	Inversion Register	0-3	This Register sets the inversion status for the 4 invertable relays. 1 = inverted. / Bit 0 = Relay 1 / Bit 1 = Relay 2			/*	23	*/	{	REL1	,	0	,	1	}	,	/*	REL1 Module Inversion Register	0-3	*/
40025	24	REL	2	Inversion Register	0-3	This Register sets the inversion status for the 4 invertable relays. 1 = inverted. / Bit 0 = Relay 1 / Bit 1 = Relay 2			/*	24	*/	{	REL2	,	0	,	1	}	,	/*	REL2 Module Inversion Register	0-3	*/
40026	25	REL	3	Inversion Register	0-3	This Register sets the inversion status for the 4 invertable relays. 1 = inverted.Bit 0 = PFC1Bit 1 = PFC4			/*	25	*/	{	REL3	,	0	,	1	}	,	/*	REL3 Module Inversion Register	0-3	*/
40027	26	REL	4	Inversion Register	0-3	This Register sets the inversion status for the 4 invertable relays. 1 = inverted.Bit 0 = PFC1Bit 1 = PFC5			/*	26	*/	{	REL4	,	0	,	1	}	,	/*	REL4 Module Inversion Register	0-3	*/
40028	27	TMP	1	Config Register		Bit 0: 0=Temp single read 1= Avg of 10 tmps/second			/*	27	*/	{	TMP1	,	0	,	1	}	,	/*	TMP1 Module Config Register	0	*/
40029	28	TMP	2	Config Register		Bit 0: 0=Temp single read 1= Avg of 10 tmps/second			/*	28	*/	{	TMP2	,	0	,	1	}	,	/*	TMP2 Module Config Register	0	*/
40030	29	TMP	3	Config Register		Bit 0: 0=Temp single read 1= Avg of 10 tmps/second			/*	29	*/	{	TMP3	,	0	,	1	}	,	/*	TMP3 Module Config Register	0	*/
40031	30	PWM	1	Frequency	24-1500 Hz	Sets the PWM Frequency of PWM Module 0			/*	30	*/	{	PWM1	,	0	,	1	}	,	/*	PWM1 Module Frequency	24-1500 Hz	*/
40032	31	PWM	2	Frequency	24-1500 Hz	Sets the PWM Frequency of PWM Module 1			/*	31	*/	{	PWM2	,	0	,	1	}	,	/*	PWM2 Module Frequency	24-1500 Hz	*/
40033	32	PWM	3	Frequency	24-1500 Hz	Sets the PWM Frequency of PWM Module 2			/*	32	*/	{	PWM3	,	0	,	1	}	,	/*	PWM3 Module Frequency	24-1500 Hz	*/
40034	33	PWM	4	Frequency	24-1500 Hz	Sets the PWM Frequency of PWM Module 3			/*	33	*/	{	PWM4	,	0	,	1	}	,	/*	PWM4 Module Frequency	24-1500 Hz	*/
40035	34	PWM	5	Frequency	24-1500 Hz	Sets the PWM Frequency of PWM Module 4			/*	34	*/	{	PWM5	,	0	,	1	}	,	/*	PWM5 Module Frequency	24-1500 Hz	*/
40036	35	PWM	6	Frequency	24-1500 Hz	Sets the PWM Frequency of PWM Module 5			/*	35	*/	{	PWM6	,	0	,	1	}	,	/*	PWM6 Module Frequency	24-1500 Hz	*/
40037	36	PWM	7	Frequency	24-1500 Hz	Sets the PWM Frequency of PWM Module 6			/*	36	*/	{	PWM7	,	0	,	1	}	,	/*	PWM7 Module Frequency	24-1500 Hz	*/
40038	37	PWM	8	Frequency	24-1500 Hz	Sets the PWM Frequency of PWM Module 7			/*	37	*/	{	PWM8	,	0	,	1	}	,	/*	PWM8 Module Frequency	24-1500 Hz	*/
40039	38	PWM	1	Duty Cycle 1	0-100 %	Duty Cycle of the PWM Output in Percent			/*	38	*/	{	PWM1	,	1	,	0	}	,	/*	PWM1 Module Duty Cycle 1	0-100 %	*/
40040	39	PWM	1	Duty Cycle 2	0-100 %	Duty Cycle of the PWM Output in Percent			/*	39	*/	{	PWM1	,	2	,	0	}	,	/*	PWM1 Module Duty Cycle 2	0-100 %	*/
40041	40	PWM	1	Duty Cycle 3	0-100 %	Duty Cycle of the PWM Output in Percent			/*	40	*/	{	PWM1	,	3	,	0	}	,	/*	PWM1 Module Duty Cycle 3	0-100 %	*/
40042	41	PWM	1	Duty Cycle 4	0-100 %	Duty Cycle of the PWM Output in Percent			/*	41	*/	{	PWM1	,	4	,	0	}	,	/*	PWM1 Module Duty Cycle 4	0-100 %	*/
40043	42	PWM	2	Duty Cycle 1	0-100 %	Duty Cycle of the PWM Output in Percent			/*	42	*/	{	PWM2	,	1	,	0	}	,	/*	PWM2 Module Duty Cycle 1	0-100 %	*/
40044	43	PWM	2	Duty Cycle 2	0-100 %	Duty Cycle of the PWM Output in Percent			/*	43	*/	{	PWM2	,	2	,	0	}	,	/*	PWM2 Module Duty Cycle 2	0-100 %	*/
40045	44	PWM	2	Duty Cycle 3	0-100 %	Duty Cycle of the PWM Output in Percent			/*	44	*/	{	PWM2	,	3	,	0	}	,	/*	PWM2 Module Duty Cycle 3	0-100 %	*/
40046	45	PWM	2	Duty Cycle 4	0-100 %	Duty Cycle of the PWM Output in Percent			/*	45	*/	{	PWM2	,	4	,	0	}	,	/*	PWM2 Module Duty Cycle 4	0-100 %	*/
40047	46	PWM	3	Duty Cycle 1	0-100 %	Duty Cycle of the PWM Output in Percent			/*	46	*/	{	PWM3	,	1	,	0	}	,	/*	PWM3 Module Duty Cycle 1	0-100 %	*/
40048	47	PWM	3	Duty Cycle 2	0-100 %	Duty Cycle of the PWM Output in Percent			/*	47	*/	{	PWM3	,	2	,	0	}	,	/*	PWM3 Module Duty Cycle 2	0-100 %	*/
40049	48	PWM	3	Duty Cycle 3	0-100 %	Duty Cycle of the PWM Output in Percent			/*	48	*/	{	PWM3	,	3	,	0	}	,	/*	PWM3 Module Duty Cycle 3	0-100 %	*/
40050	49	PWM	3	Duty Cycle 4	0-100 %	Duty Cycle of the PWM Output in Percent			/*	49	*/	{	PWM3	,	4	,	0	}	,	/*	PWM3 Module Duty Cycle 4	0-100 %	*/
40051	50	PWM	4	Duty Cycle 1	0-100 %	Duty Cycle of the PWM Output in Percent			/*	50	*/	{	PWM4	,	1	,	0	}	,	/*	PWM4 Module Duty Cycle 1	0-100 %	*/
40052	51	PWM	4	Duty Cycle 2	0-100 %	Duty Cycle of the PWM Output in Percent			/*	51	*/	{	PWM4	,	2	,	0	}	,	/*	PWM4 Module Duty Cycle 2	0-100 %	*/
40053	52	PWM	4	Duty Cycle 3	0-100 %	Duty Cycle of the PWM Output in Percent			/*	52	*/	{	PWM4	,	3	,	0	}	,	/*	PWM4 Module Duty Cycle 3	0-100 %	*/
40054	53	PWM	4	Duty Cycle 4	0-100 %	Duty Cycle of the PWM Output in Percent			/*	53	*/	{	PWM4	,	4	,	0	}	,	/*	PWM4 Module Duty Cycle 4	0-100 %	*/
40055	54	PWM	5	Duty Cycle 1	0-100 %	Duty Cycle of the PWM Output in Percent			/*	54	*/	{	PWM5	,	1	,	0	}	,	/*	PWM5 Module Duty Cycle 1	0-100 %	*/
40056	55	PWM	5	Duty Cycle 2	0-100 %	Duty Cycle of the PWM Output in Percent			/*	55	*/	{	PWM5	,	2	,	0	}	,	/*	PWM5 Module Duty Cycle 2	0-100 %	*/
40057	56	PWM	5	Duty Cycle 3	0-100 %	Duty Cycle of the PWM Output in Percent			/*	56	*/	{	PWM5	,	3	,	0	}	,	/*	PWM5 Module Duty Cycle 3	0-100 %	*/
40058	57	PWM	5	Duty Cycle 4	0-100 %	Duty Cycle of the PWM Output in Percent			/*	57	*/	{	PWM5	,	4	,	0	}	,	/*	PWM5 Module Duty Cycle 4	0-100 %	*/
40059	58	PWM	6	Duty Cycle 1	0-100 %	Duty Cycle of the PWM Output in Percent			/*	58	*/	{	PWM6	,	1	,	0	}	,	/*	PWM6 Module Duty Cycle 1	0-100 %	*/
40060	59	PWM	6	Duty Cycle 2	0-100 %	Duty Cycle of the PWM Output in Percent			/*	59	*/	{	PWM6	,	2	,	0	}	,	/*	PWM6 Module Duty Cycle 2	0-100 %	*/
40061	60	PWM	6	Duty Cycle 3	0-100 %	Duty Cycle of the PWM Output in Percent			/*	60	*/	{	PWM6	,	3	,	0	}	,	/*	PWM6 Module Duty Cycle 3	0-100 %	*/
40062	61	PWM	6	Duty Cycle 4	0-100 %	Duty Cycle of the PWM Output in Percent			/*	61	*/	{	PWM6	,	4	,	0	}	,	/*	PWM6 Module Duty Cycle 4	0-100 %	*/
40063	62	PWM	7	Duty Cycle 1	0-100 %	Duty Cycle of the PWM Output in Percent			/*	62	*/	{	PWM7	,	1	,	0	}	,	/*	PWM7 Module Duty Cycle 1	0-100 %	*/
40064	63	PWM	7	Duty Cycle 2	0-100 %	Duty Cycle of the PWM Output in Percent			/*	63	*/	{	PWM7	,	2	,	0	}	,	/*	PWM7 Module Duty Cycle 2	0-100 %	*/
40065	64	PWM	7	Duty Cycle 3	0-100 %	Duty Cycle of the PWM Output in Percent			/*	64	*/	{	PWM7	,	3	,	0	}	,	/*	PWM7 Module Duty Cycle 3	0-100 %	*/
40066	65	PWM	7	Duty Cycle 4	0-100 %	Duty Cycle of the PWM Output in Percent			/*	65	*/	{	PWM7	,	4	,	0	}	,	/*	PWM7 Module Duty Cycle 4	0-100 %	*/
40067	66	PWM	8	Duty Cycle 1	0-100 %	Duty Cycle of the PWM Output in Percent			/*	66	*/	{	PWM8	,	1	,	0	}	,	/*	PWM8 Module Duty Cycle 1	0-100 %	*/
40068	67	PWM	8	Duty Cycle 2	0-100 %	Duty Cycle of the PWM Output in Percent			/*	67	*/	{	PWM8	,	2	,	0	}	,	/*	PWM8 Module Duty Cycle 2	0-100 %	*/
40069	68	PWM	8	Duty Cycle 3	0-100 %	Duty Cycle of the PWM Output in Percent			/*	68	*/	{	PWM8	,	3	,	0	}	,	/*	PWM8 Module Duty Cycle 3	0-100 %	*/
40070	69	PWM	8	Duty Cycle 4	0-100 %	Duty Cycle of the PWM Output in Percent			/*	69	*/	{	PWM8	,	4	,	0	}	,	/*	PWM8 Module Duty Cycle 4	0-100 %	*/
40071	70	REL	1	All Relays	0x00 – 0xFF	The first 8 bits of this register describe the status of the 8 relays on the module. A set / Bit turns the relay on. / Relays will be inverted according to REL Modul Inversion Register			/*	70	*/	{	REL1	,	1	,	0	}	,	/*	REL1 Module All Relays	0x00 – 0xFF	*/
40072	71	REL	2	All Relays	0x00 – 0xFF	The first 8 bits of this register describe the status of the 8 relays on the module. A set / Bit turns the relay on. / Relays will be inverted according to REL Modul Inversion Register			/*	71	*/	{	REL2	,	1	,	0	}	,	/*	REL2 Module All Relays	0x00 – 0xFF	*/
40073	72	REL	3	All Relays	0x00 – 0xFF	The first 8 bits of this register describe the status of the 8 relays on the module. A set / Bit turns the relay on. / Relays will be inverted according to REL Modul Inversion Register			/*	72	*/	{	REL3	,	1	,	0	}	,	/*	REL3 Module All Relays	0x00 – 0xFF	*/
40074	73	REL	4	All Relays	0x00 – 0xFF	The first 8 bits of this register describe the status of the 8 relays on the module. A set / Bit turns the relay on. / Relays will be inverted according to REL Modul Inversion Register			/*	73	*/	{	REL4	,	1	,	0	}	,	/*	REL4 Module All Relays	0x00 – 0xFF	*/
40075	74	AIO	1	Pecentual Output 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 1 Config (ADRESS). / The Value has to be multiplied by 10 (dezipercent → 100% = 1000)			/*	74	*/	{	AIO1	,	1	,	0	}	,	/*	AIO1 Module Pecentual Output 1	0.0-100.0%	*/
40076	75	AIO	1	Pecentual Output 2	0.0-100.0%	as above			/*	75	*/	{	AIO1	,	2	,	0	}	,	/*	AIO1 Module Pecentual Output 2	0.0-100.0%	*/
40077	76	AIO	1	Pecentual Output 3	0.0-100.0%	as above			/*	76	*/	{	AIO1	,	3	,	0	}	,	/*	AIO1 Module Pecentual Output 3	0.0-100.0%	*/
40078	77	AIO	1	Pecentual Output 4	0.0-100.0%	as above			/*	77	*/	{	AIO1	,	4	,	0	}	,	/*	AIO1 Module Pecentual Output 4	0.0-100.0%	*/
40079	78	AIO	2	Pecentual Output 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 2 Config (ADRESS). / The Value has to be multiplied by 10 (dezipercent → 100% = 1000)			/*	78	*/	{	AIO2	,	1	,	0	}	,	/*	AIO2 Module Pecentual Output 1	0.0-100.0%	*/
40080	79	AIO	2	Pecentual Output 2	0.0-100.0%	The Value has to be multiplied by 10 (dezipercent → 100% = 1000)			/*	79	*/	{	AIO2	,	2	,	0	}	,	/*	AIO2 Module Pecentual Output 2	0.0-100.0%	*/
40081	80	AIO	2	Pecentual Output 3	0.0-100.0%	as above			/*	80	*/	{	AIO2	,	3	,	0	}	,	/*	AIO2 Module Pecentual Output 3	0.0-100.0%	*/
40082	81	AIO	2	Pecentual Output 4	0.0-100.0%	as above			/*	81	*/	{	AIO2	,	4	,	0	}	,	/*	AIO2 Module Pecentual Output 4	0.0-100.0%	*/
40083	82	AIO	3	Pecentual Output 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 3 Config (ADRESS). / The Value has to be multiplied by 10 (dezipercent → 100% = 1000)			/*	82	*/	{	AIO3	,	1	,	0	}	,	/*	AIO3 Module Pecentual Output 1	0.0-100.0%	*/
40084	83	AIO	3	Pecentual Output 2	0.0-100.0%	The Value has to be multiplied by 10 (dezipercent → 100% = 1000)			/*	83	*/	{	AIO3	,	2	,	0	}	,	/*	AIO3 Module Pecentual Output 2	0.0-100.0%	*/
40085	84	AIO	3	Pecentual Output 3	0.0-100.0%	as above			/*	84	*/	{	AIO3	,	3	,	0	}	,	/*	AIO3 Module Pecentual Output 3	0.0-100.0%	*/
40086	85	AIO	3	Pecentual Output 4	0.0-100.0%	as above			/*	85	*/	{	AIO3	,	4	,	0	}	,	/*	AIO3 Module Pecentual Output 4	0.0-100.0%	*/
40087	86	AIO	4	Pecentual Output 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 4 Config (ADRESS). / The Value has to be multiplied by 10 (dezipercent → 100% = 1000)			/*	86	*/	{	AIO4	,	1	,	0	}	,	/*	AIO4 Module Pecentual Output 1	0.0-100.0%	*/
40088	87	AIO	4	Pecentual Output 2	0.0-100.0%	The Value has to be multiplied by 10 (dezipercent → 100% = 1000)			/*	87	*/	{	AIO4	,	2	,	0	}	,	/*	AIO4 Module Pecentual Output 2	0.0-100.0%	*/
40089	88	AIO	4	Pecentual Output 3	0.0-100.0%	as above			/*	88	*/	{	AIO4	,	3	,	0	}	,	/*	AIO4 Module Pecentual Output 3	0.0-100.0%	*/
40090	89	AIO	4	Pecentual Output 4	0.0-100.0%	as above			/*	89	*/	{	AIO4	,	4	,	0	}	,	/*	AIO4 Module Pecentual Output 4	0.0-100.0%	*/
40091	90	AIO	5	Pecentual Output 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 5 Config (ADRESS). / The Value has to be multiplied by 10 (dezipercent → 100% = 1000)			/*	90	*/	{	AIO5	,	1	,	0	}	,	/*	AIO5 Module Pecentual Output 1	0.0-100.0%	*/
40092	91	AIO	5	Pecentual Output 2	0.0-100.0%	as above			/*	91	*/	{	AIO5	,	2	,	0	}	,	/*	AIO5 Module Pecentual Output 2	0.0-100.0%	*/
40093	92	AIO	5	Pecentual Output 3	0.0-100.0%	as above			/*	92	*/	{	AIO5	,	3	,	0	}	,	/*	AIO5 Module Pecentual Output 3	0.0-100.0%	*/
40094	93	AIO	5	Pecentual Output 4	0.0-100.0%	as above			/*	93	*/	{	AIO5	,	4	,	0	}	,	/*	AIO5 Module Pecentual Output 4	0.0-100.0%	*/
40095	94	AIO	6	Pecentual Output 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 6 Config (ADRESS). / The Value has to be multiplied by 10 (dezipercent → 100% = 1000)			/*	94	*/	{	AIO6	,	1	,	0	}	,	/*	AIO6 Module Pecentual Output 1	0.0-100.0%	*/
40096	95	AIO	6	Pecentual Output 2	0.0-100.0%	as above			/*	95	*/	{	AIO6	,	2	,	0	}	,	/*	AIO6 Module Pecentual Output 2	0.0-100.0%	*/
40097	96	AIO	6	Pecentual Output 3	0.0-100.0%	as above			/*	96	*/	{	AIO6	,	3	,	0	}	,	/*	AIO6 Module Pecentual Output 3	0.0-100.0%	*/
40098	97	AIO	6	Pecentual Output 4	0.0-100.0%	as above			/*	97	*/	{	AIO6	,	4	,	0	}	,	/*	AIO6 Module Pecentual Output 4	0.0-100.0%	*/
40099	98	AIO	7	Pecentual Output 1	0.0-100.0%	This is encoded to 16 bit unsigned integer. Percentual Value of connected Device that automaticaly utilizes the Interface set in AIO Modul 7 Config (ADRESS). / The Value has to be multiplied by 10 (dezipercent → 100% = 1000)			/*	98	*/	{	AIO7	,	1	,	0	}	,	/*	AIO7 Module Pecentual Output 1	0.0-100.0%	*/
40100	99	AIO	7	Pecentual Output 2	0.0-100.0%	as above			/*	99	*/	{	AIO7	,	2	,	0	}	,	/*	AIO7 Module Pecentual Output 2	0.0-100.0%	*/
40101	100	AIO	7	Pecentual Output 3	0.0-100.0%	as above			/*	100	*/	{	AIO7	,	3	,	0	}	,	/*	AIO7 Module Pecentual Output 3	0.0-100.0%	*/
40102	101	AIO	7	Pecentual Output 4	0.0-100.0%	as above			/*	101	*/	{	AIO7	,	4	,	0	}	,	/*	AIO7 Module Pecentual Output 4	0.0-100.0%	*/
40103	102	AIO	1	Voltage Output 1	0-10.000 mV	Voltage in millivolt that will be outputet on AIO Modul 1.			/*	102	*/	{	AIO1	,	5	,	0	}	,	/*	AIO1 Module Voltage Output 1	0-10.000 mV	*/
40104	103	AIO	1	Voltage Output 2	0-10.000 mV	as above			/*	103	*/	{	AIO1	,	6	,	0	}	,	/*	AIO1 Module Voltage Output 2	0-10.000 mV	*/
40105	104	AIO	1	Voltage Output 3	0-10.000 mV	as above			/*	104	*/	{	AIO1	,	7	,	0	}	,	/*	AIO1 Module Voltage Output 3	0-10.000 mV	*/
40106	105	AIO	1	Voltage Output 4	0-10.000 mV	as above			/*	105	*/	{	AIO1	,	8	,	0	}	,	/*	AIO1 Module Voltage Output 4	0-10.000 mV	*/
40107	106	AIO	2	Voltage Output 1	0-10.000 mV	Voltage in millivolt that will be outputet on AIO Modul 2.			/*	106	*/	{	AIO2	,	5	,	0	}	,	/*	AIO2 Module Voltage Output 1	0-10.000 mV	*/
40108	107	AIO	2	Voltage Output 2	0-10.000 mV	as above			/*	107	*/	{	AIO2	,	6	,	0	}	,	/*	AIO2 Module Voltage Output 2	0-10.000 mV	*/
40109	108	AIO	2	Voltage Output 3	0-10.000 mV	as above			/*	108	*/	{	AIO2	,	7	,	0	}	,	/*	AIO2 Module Voltage Output 3	0-10.000 mV	*/
40110	109	AIO	2	Voltage Output 4	0-10.000 mV	as above			/*	109	*/	{	AIO2	,	8	,	0	}	,	/*	AIO2 Module Voltage Output 4	0-10.000 mV	*/
40111	110	AIO	3	Voltage Output 1	0-10.000 mV	Voltage in millivolt that will be outputet on AIO Modul 3.			/*	110	*/	{	AIO3	,	5	,	0	}	,	/*	AIO3 Module Voltage Output 1	0-10.000 mV	*/
40112	111	AIO	3	Voltage Output 2	0-10.000 mV	as above			/*	111	*/	{	AIO3	,	6	,	0	}	,	/*	AIO3 Module Voltage Output 2	0-10.000 mV	*/
40113	112	AIO	3	Voltage Output 3	0-10.000 mV	as above			/*	112	*/	{	AIO3	,	7	,	0	}	,	/*	AIO3 Module Voltage Output 3	0-10.000 mV	*/
40114	113	AIO	3	Voltage Output 4	0-10.000 mV	as above			/*	113	*/	{	AIO3	,	8	,	0	}	,	/*	AIO3 Module Voltage Output 4	0-10.000 mV	*/
40115	114	AIO	4	Voltage Output 1	0-10.000 mV	Voltage in millivolt that will be outputet on AIO Modul 4.			/*	114	*/	{	AIO4	,	5	,	0	}	,	/*	AIO4 Module Voltage Output 1	0-10.000 mV	*/
40116	115	AIO	4	Voltage Output 2	0-10.000 mV	as above			/*	115	*/	{	AIO4	,	6	,	0	}	,	/*	AIO4 Module Voltage Output 2	0-10.000 mV	*/
40117	116	AIO	4	Voltage Output 3	0-10.000 mV	as above			/*	116	*/	{	AIO4	,	7	,	0	}	,	/*	AIO4 Module Voltage Output 3	0-10.000 mV	*/
40118	117	AIO	4	Voltage Output 4	0-10.000 mV	as above			/*	117	*/	{	AIO4	,	8	,	0	}	,	/*	AIO4 Module Voltage Output 4	0-10.000 mV	*/
40119	118	AIO	5	Voltage Output 1	0-10.000 mV	Voltage in millivolt that will be outputet on AIO Modul 5.			/*	118	*/	{	AIO5	,	5	,	0	}	,	/*	AIO5 Module Voltage Output 1	0-10.000 mV	*/
40120	119	AIO	5	Voltage Output 2	0-10.000 mV	as above			/*	119	*/	{	AIO5	,	6	,	0	}	,	/*	AIO5 Module Voltage Output 2	0-10.000 mV	*/
40121	120	AIO	5	Voltage Output 3	0-10.000 mV	as above			/*	120	*/	{	AIO5	,	7	,	0	}	,	/*	AIO5 Module Voltage Output 3	0-10.000 mV	*/
40122	121	AIO	5	Voltage Output 4	0-10.000 mV	as above			/*	121	*/	{	AIO5	,	8	,	0	}	,	/*	AIO5 Module Voltage Output 4	0-10.000 mV	*/
40123	122	AIO	6	Voltage Output 1	0-10.000 mV	Voltage in millivolt that will be outputet on AIO Modul 6.			/*	122	*/	{	AIO6	,	5	,	0	}	,	/*	AIO6 Module Voltage Output 1	0-10.000 mV	*/
40124	123	AIO	6	Voltage Output 2	0-10.000 mV	as above			/*	123	*/	{	AIO6	,	6	,	0	}	,	/*	AIO6 Module Voltage Output 2	0-10.000 mV	*/
40125	124	AIO	6	Voltage Output 3	0-10.000 mV	as above			/*	124	*/	{	AIO6	,	7	,	0	}	,	/*	AIO6 Module Voltage Output 3	0-10.000 mV	*/
40126	125	AIO	6	Voltage Output 4	0-10.000 mV	as above			/*	125	*/	{	AIO6	,	8	,	0	}	,	/*	AIO6 Module Voltage Output 4	0-10.000 mV	*/
40127	126	AIO	7	Voltage Output 1	0-10.000 mV	Voltage in millivolt that will be outputet on AIO Modul 7.			/*	126	*/	{	AIO7	,	5	,	0	}	,	/*	AIO7 Module Voltage Output 1	0-10.000 mV	*/
40128	127	AIO	7	Voltage Output 2	0-10.000 mV	as above			/*	127	*/	{	AIO7	,	6	,	0	}	,	/*	AIO7 Module Voltage Output 2	0-10.000 mV	*/
40129	128	AIO	7	Voltage Output 3	0-10.000 mV	as above			/*	128	*/	{	AIO7	,	7	,	0	}	,	/*	AIO7 Module Voltage Output 3	0-10.000 mV	*/
40130	129	AIO	7	Voltage Output 4	0-10.000 mV	as above			/*	129	*/	{	AIO7	,	8	,	0	}	,	/*	AIO7 Module Voltage Output 4	0-10.000 mV	*/
40131	130	AIO	1	Current Output 1	0-20000 mA	Current in milli Ampere that will be outputet on AIO Modul 1.			/*	130	*/	{	AIO1	,	9	,	0	}	,	/*	AIO1 Module Current Output 1	0-20000 mA	*/
40132	131	AIO	1	Current Output 2	0-20000 mA	as above			/*	131	*/	{	AIO1	,	10	,	0	}	,	/*	AIO1 Module Current Output 2	0-20000 mA	*/
40133	132	AIO	1	Current Output 3	0-20000 mA	as above			/*	132	*/	{	AIO1	,	11	,	0	}	,	/*	AIO1 Module Current Output 3	0-20000 mA	*/
40134	133	AIO	1	Current Output 4	0-20000 mA	as above			/*	133	*/	{	AIO1	,	12	,	0	}	,	/*	AIO1 Module Current Output 4	0-20000 mA	*/
40135	134	AIO	2	Current Output 1	0-20000 mA	Current in milli Ampere that will be outputet on AIO Modul 2.			/*	134	*/	{	AIO2	,	9	,	0	}	,	/*	AIO2 Module Current Output 1	0-20000 mA	*/
40136	135	AIO	2	Current Output 2	0-20000 mA	as above			/*	135	*/	{	AIO2	,	10	,	0	}	,	/*	AIO2 Module Current Output 2	0-20000 mA	*/
40137	136	AIO	2	Current Output 3	0-20000 mA	as above			/*	136	*/	{	AIO2	,	11	,	0	}	,	/*	AIO2 Module Current Output 3	0-20000 mA	*/
40138	137	AIO	2	Current Output 4	0-20000 mA	as above			/*	137	*/	{	AIO2	,	12	,	0	}	,	/*	AIO2 Module Current Output 4	0-20000 mA	*/
40139	138	AIO	3	Current Output 1	0-20000 mA	Current in milli Ampere that will be outputet on AIO Modul 3.			/*	138	*/	{	AIO3	,	9	,	0	}	,	/*	AIO3 Module Current Output 1	0-20000 mA	*/
40140	139	AIO	3	Current Output 2	0-20000 mA	as above			/*	139	*/	{	AIO3	,	10	,	0	}	,	/*	AIO3 Module Current Output 2	0-20000 mA	*/
40141	140	AIO	3	Current Output 3	0-20000 mA	as above			/*	140	*/	{	AIO3	,	11	,	0	}	,	/*	AIO3 Module Current Output 3	0-20000 mA	*/
40142	141	AIO	3	Current Output 4	0-20000 mA	as above			/*	141	*/	{	AIO3	,	12	,	0	}	,	/*	AIO3 Module Current Output 4	0-20000 mA	*/
40143	142	AIO	4	Current Output 1	0-20000 mA	Current in milli Ampere that will be outputet on AIO Modul 4.			/*	142	*/	{	AIO4	,	9	,	0	}	,	/*	AIO4 Module Current Output 1	0-20000 mA	*/
40144	143	AIO	4	Current Output 2	0-20000 mA	as above			/*	143	*/	{	AIO4	,	10	,	0	}	,	/*	AIO4 Module Current Output 2	0-20000 mA	*/
40145	144	AIO	4	Current Output 3	0-20000 mA	as above			/*	144	*/	{	AIO4	,	11	,	0	}	,	/*	AIO4 Module Current Output 3	0-20000 mA	*/
40146	145	AIO	4	Current Output 4	0-20000 mA	as above			/*	145	*/	{	AIO4	,	12	,	0	}	,	/*	AIO4 Module Current Output 4	0-20000 mA	*/
40147	146	AIO	5	Current Output 1	0-20000 mA	Current in milli Ampere that will be outputet on AIO Modul 5.			/*	146	*/	{	AIO5	,	9	,	0	}	,	/*	AIO5 Module Current Output 1	0-20000 mA	*/
40148	147	AIO	5	Current Output 2	0-20000 mA	as above			/*	147	*/	{	AIO5	,	10	,	0	}	,	/*	AIO5 Module Current Output 2	0-20000 mA	*/
40149	148	AIO	5	Current Output 3	0-20000 mA	as above			/*	148	*/	{	AIO5	,	11	,	0	}	,	/*	AIO5 Module Current Output 3	0-20000 mA	*/
40150	149	AIO	5	Current Output 4	0-20000 mA	as above			/*	149	*/	{	AIO5	,	12	,	0	}	,	/*	AIO5 Module Current Output 4	0-20000 mA	*/
40151	150	AIO	6	Current Output 1	0-20000 mA	Current in milli Ampere that will be outputet on AIO Modul 6.			/*	150	*/	{	AIO6	,	9	,	0	}	,	/*	AIO6 Module Current Output 1	0-20000 mA	*/
40152	151	AIO	6	Current Output 2	0-20000 mA	as above			/*	151	*/	{	AIO6	,	10	,	0	}	,	/*	AIO6 Module Current Output 2	0-20000 mA	*/
40153	152	AIO	6	Current Output 3	0-20000 mA	as above			/*	152	*/	{	AIO6	,	11	,	0	}	,	/*	AIO6 Module Current Output 3	0-20000 mA	*/
40154	153	AIO	6	Current Output 4	0-20000 mA	as above			/*	153	*/	{	AIO6	,	12	,	0	}	,	/*	AIO6 Module Current Output 4	0-20000 mA	*/
40155	154	AIO	7	Current Output 1	0-20000 mA	Current in milli Ampere that will be outputet on AIO Modul 7.			/*	154	*/	{	AIO7	,	9	,	0	}	,	/*	AIO7 Module Current Output 1	0-20000 mA	*/
40156	155	AIO	7	Current Output 2	0-20000 mA	as above			/*	155	*/	{	AIO7	,	10	,	0	}	,	/*	AIO7 Module Current Output 2	0-20000 mA	*/
40157	156	AIO	7	Current Output 3	0-20000 mA	as above			/*	156	*/	{	AIO7	,	11	,	0	}	,	/*	AIO7 Module Current Output 3	0-20000 mA	*/
40158	157	AIO	7	Current Output 4	0-20000 mA	as above			/*	157	*/	{	AIO7	,	12	,	0	}	,	/*	AIO7 Module Current Output 4	0-20000 mA	*/

				};

## CSV
Version	0.7.12
Modbus Offset	Discrete Output Modul Typ	Discrete Output ModulNr	Discrete Output Mreg	Discrete Input Modul Typ	Discrete Input ModulNr	Discrete Input Mreg	Input Register Modul Typ	Input Register ModulNr	Input Register Mreg	Output Register Modul Typ	Output Register ModulNr	Output Register Mreg
0	LEAFLET	0	0	LEAFLET	0	0	LEAFLET	0	0	LEAFLET	0	0
1	LEAFLET	0	1	LEAFLET	0	1	LEAFLET	0	1	LEAFLET	0	1
2	LEAFLET	0	2	LEAFLET	0	2	LEAFLET	0	2	LEAFLET	0	2
3	LEAFLET	0	3	LEAFLET	0	3	LEAFLET	0	3	LEAFLET	0	3
4	LEAFLET	0	4	LEAFLET	0	4	LEAFLET	0	4	LEAFLET	0	4
5	LEAFLET	0	5	LEAFLET	0	5	LEAFLET	0	5	LEAFLET	0	5
6	LEAFLET	0	6	LEAFLET	0	6	LEAFLET	0	6	LEAFLET	0	6
7	LEAFLET	0	7	LEAFLET	0	7	LEAFLET	0	7	LEAFLET	0	7
8	LEAFLET	0	8	LEAFLET	0	8	LEAFLET	0	8	LEAFLET	0	8
9	LEAFLET	0	9	LEAFLET	0	9	LEAFLET	0	9	LEAFLET	0	9
10	LEAFLET	0	10	LEAFLET	0	10	LEAFLET	0	10	LEAFLET	0	10
11	LEAFLET	0	11	LEAFLET	0	11	LEAFLET	0	11	LEAFLET	0	11
12	LEAFLET	0	12	LEAFLET	0	12	LEAFLET	0	12	LEAFLET	0	12
13	LEAFLET	0	13	LEAFLET	0	13	LEAFLET	0	13	LEAFLET	0	13
14	LEAFLET	0	14	LEAFLET	0	14	LEAFLET	0	14	LEAFLET	0	14
15	LEAFLET	0	15	LEAFLET	0	15	LEAFLET	0	15	LEAFLET	0	15
16	PWM	1	0	AIO	1	0	PWM	1	0	AIO	1	0
17	PWM	1	1	AIO	1	1	PWM	2	0	AIO	2	0
18	PWM	1	2	AIO	1	2	PWM	3	0	AIO	3	0
19	PWM	1	3	AIO	1	3	PWM	4	0	AIO	4	0
20	PWM	2	0	AIO	2	0	PWM	5	0	AIO	5	0
21	PWM	2	1	AIO	2	1	PWM	6	0	AIO	6	0
22	PWM	2	2	AIO	2	2	PWM	7	0	AIO	7	0
23	PWM	2	3	AIO	2	3	PWM	8	0	REL	1	0
24	PWM	3	0	AIO	3	0	REL	1	0	REL	2	0
25	PWM	3	1	AIO	3	1	REL	2	0	REL	3	0
26	PWM	3	2	AIO	3	2	REL	3	0	REL	4	0
27	PWM	3	3	AIO	3	3	REL	4	0	TMP	1	0
28	PWM	4	0	AIO	4	0	TMP	1	0	TMP	2	0
29	PWM	4	1	AIO	4	1	TMP	2	0	TMP	3	0
30	PWM	4	2	AIO	4	2	TMP	3	0	PWM	1	0
31	PWM	4	3	AIO	4	3	AIO	1	0	PWM	2	0
32	PWM	5	0	AIO	5	0	AIO	2	0	PWM	3	0
33	PWM	5	1	AIO	5	1	AIO	3	0	PWM	4	0
34	PWM	5	2	AIO	5	2	AIO	4	0	PWM	5	0
35	PWM	5	3	AIO	5	3	AIO	5	0	PWM	6	0
36	PWM	6	0	AIO	6	0	AIO	6	0	PWM	7	0
37	PWM	6	1	AIO	6	1	AIO	7	0	PWM	8	0
38	PWM	6	2	AIO	6	2	TMP	1	1	PWM	1	1
39	PWM	6	3	AIO	6	3	TMP	1	2	PWM	1	2
40	PWM	7	0	AIO	7	0	TMP	1	3	PWM	1	3
41	PWM	7	1	AIO	7	1	TMP	1	4	PWM	1	4
42	PWM	7	2	AIO	7	2	TMP	1	5	PWM	2	1
43	PWM	7	3	AIO	7	3	TMP	1	6	PWM	2	2
44	PWM	8	0	0	0	0	TMP	1	7	PWM	2	3
45	PWM	8	1	0	0	0	TMP	1	8	PWM	2	4
46	PWM	8	2	0	0	0	TMP	1	9	PWM	3	1
47	PWM	8	3	0	0	0	TMP	1	10	PWM	3	2
48	REL	1	0	0	0	0	TMP	1	11	PWM	3	3
49	REL	1	1	0	0	0	TMP	1	12	PWM	3	4
50	REL	1	2	0	0	0	TMP	1	13	PWM	4	1
51	REL	1	3	0	0	0	TMP	1	14	PWM	4	2
52	REL	1	4	0	0	0	TMP	1	15	PWM	4	3
53	REL	1	5	0	0	0	TMP	1	16	PWM	4	4
54	REL	1	6	0	0	0	TMP	2	1	PWM	5	1
55	REL	1	7	0	0	0	TMP	2	2	PWM	5	2
56	REL	2	0	0	0	0	TMP	2	3	PWM	5	3
57	REL	2	1	0	0	0	TMP	2	4	PWM	5	4
58	REL	2	2	0	0	0	TMP	2	5	PWM	6	1
59	REL	2	3	0	0	0	TMP	2	6	PWM	6	2
60	REL	2	4	0	0	0	TMP	2	7	PWM	6	3
61	REL	2	5	0	0	0	TMP	2	8	PWM	6	4
62	REL	2	6	0	0	0	TMP	2	9	PWM	7	1
63	REL	2	7	0	0	0	TMP	2	10	PWM	7	2
64	REL	3	0	0	0	0	TMP	2	11	PWM	7	3
65	REL	3	1	0	0	0	TMP	2	12	PWM	7	4
66	REL	3	2	0	0	0	TMP	2	13	PWM	8	1
67	REL	3	3	0	0	0	TMP	2	14	PWM	8	2
68	REL	3	4	0	0	0	TMP	2	15	PWM	8	3
69	REL	3	5	0	0	0	TMP	2	16	PWM	8	4
70	REL	3	6	0	0	0	TMP	3	1	REL	1	1
71	REL	3	7	0	0	0	TMP	3	2	REL	2	1
72	REL	4	0	0	0	0	TMP	3	3	REL	3	1
73	REL	4	1	0	0	0	TMP	3	4	REL	4	1
74	REL	4	2	0	0	0	TMP	3	5	AIO	1	1
75	REL	4	3	0	0	0	TMP	3	6	AIO	1	2
76	REL	4	4	0	0	0	TMP	3	7	AIO	1	3
77	REL	4	5	0	0	0	TMP	3	8	AIO	1	4
78	REL	4	6	0	0	0	TMP	3	9	AIO	2	1
79	REL	4	7	0	0	0	TMP	3	10	AIO	2	2
80	0	0	0	0	0	0	TMP	3	11	AIO	2	3
81	0	0	0	0	0	0	TMP	3	12	AIO	2	4
82	0	0	0	0	0	0	TMP	3	13	AIO	3	1
83	0	0	0	0	0	0	TMP	3	14	AIO	3	2
84	0	0	0	0	0	0	TMP	3	15	AIO	3	3
85	0	0	0	0	0	0	TMP	3	16	AIO	3	4
86	0	0	0	0	0	0	AIO	1	5	AIO	4	1
87	0	0	0	0	0	0	AIO	1	6	AIO	4	2
88	0	0	0	0	0	0	AIO	1	7	AIO	4	3
89	0	0	0	0	0	0	AIO	1	8	AIO	4	4
90	0	0	0	0	0	0	AIO	2	5	AIO	5	1
91	0	0	0	0	0	0	AIO	2	6	AIO	5	2
92	0	0	0	0	0	0	AIO	2	7	AIO	5	3
93	0	0	0	0	0	0	AIO	2	8	AIO	5	4
94	0	0	0	0	0	0	AIO	3	5	AIO	6	1
95	0	0	0	0	0	0	AIO	3	6	AIO	6	2
96	0	0	0	0	0	0	AIO	3	7	AIO	6	3
97	0	0	0	0	0	0	AIO	3	8	AIO	6	4
98	0	0	0	0	0	0	AIO	4	5	AIO	7	1
99	0	0	0	0	0	0	AIO	4	6	AIO	7	2
100	0	0	0	0	0	0	AIO	4	7	AIO	7	3
101	0	0	0	0	0	0	AIO	4	8	AIO	7	4
102	0	0	0	0	0	0	AIO	5	5	AIO	1	5
103	0	0	0	0	0	0	AIO	5	6	AIO	1	6
104	0	0	0	0	0	0	AIO	5	7	AIO	1	7
105	0	0	0	0	0	0	AIO	5	8	AIO	1	8
106	0	0	0	0	0	0	AIO	6	5	AIO	2	5
107	0	0	0	0	0	0	AIO	6	6	AIO	2	6
108	0	0	0	0	0	0	AIO	6	7	AIO	2	7
109	0	0	0	0	0	0	AIO	6	8	AIO	2	8
110	0	0	0	0	0	0	AIO	7	5	AIO	3	5
111	0	0	0	0	0	0	AIO	7	6	AIO	3	6
112	0	0	0	0	0	0	AIO	7	7	AIO	3	7
113	0	0	0	0	0	0	AIO	7	8	AIO	3	8
114	0	0	0	0	0	0	AIO	1	1	AIO	4	5
115	0	0	0	0	0	0	AIO	1	2	AIO	4	6
116	0	0	0	0	0	0	AIO	1	3	AIO	4	7
117	0	0	0	0	0	0	AIO	1	4	AIO	4	8
118	0	0	0	0	0	0	AIO	2	1	AIO	5	5
119	0	0	0	0	0	0	AIO	2	2	AIO	5	6
120	0	0	0	0	0	0	AIO	2	3	AIO	5	7
121	0	0	0	0	0	0	AIO	2	4	AIO	5	8
122	0	0	0	0	0	0	AIO	3	1	AIO	6	5
123	0	0	0	0	0	0	AIO	3	2	AIO	6	6
124	0	0	0	0	0	0	AIO	3	3	AIO	6	7
125	0	0	0	0	0	0	AIO	3	4	AIO	6	8
126	0	0	0	0	0	0	AIO	4	1	AIO	7	5
127	0	0	0	0	0	0	AIO	4	2	AIO	7	6
128	0	0	0	0	0	0	AIO	4	3	AIO	7	7
129	0	0	0	0	0	0	AIO	4	4	AIO	7	8
130	0	0	0	0	0	0	AIO	5	1	AIO	1	9
131	0	0	0	0	0	0	AIO	5	2	AIO	1	10
132	0	0	0	0	0	0	AIO	5	3	AIO	1	11
133	0	0	0	0	0	0	AIO	5	4	AIO	1	12
134	0	0	0	0	0	0	AIO	6	1	AIO	2	9
135	0	0	0	0	0	0	AIO	6	2	AIO	2	10
136	0	0	0	0	0	0	AIO	6	3	AIO	2	11
137	0	0	0	0	0	0	AIO	6	4	AIO	2	12
138	0	0	0	0	0	0	AIO	7	1	AIO	3	9
139	0	0	0	0	0	0	AIO	7	2	AIO	3	10
140	0	0	0	0	0	0	AIO	7	3	AIO	3	11
141	0	0	0	0	0	0	AIO	7	4	AIO	3	12
142	0	0	0	0	0	0	AIO	1	9	AIO	4	9
143	0	0	0	0	0	0	AIO	1	10	AIO	4	10
144	0	0	0	0	0	0	AIO	1	11	AIO	4	11
145	0	0	0	0	0	0	AIO	1	12	AIO	4	12
146	0	0	0	0	0	0	AIO	2	9	AIO	5	9
147	0	0	0	0	0	0	AIO	2	10	AIO	5	10
148	0	0	0	0	0	0	AIO	2	11	AIO	5	11
149	0	0	0	0	0	0	AIO	2	12	AIO	5	12
150	0	0	0	0	0	0	AIO	3	9	AIO	6	9
151	0	0	0	0	0	0	AIO	3	10	AIO	6	10
152	0	0	0	0	0	0	AIO	3	11	AIO	6	11
153	0	0	0	0	0	0	AIO	3	12	AIO	6	12
154	0	0	0	0	0	0	AIO	4	9	AIO	7	9
155	0	0	0	0	0	0	AIO	4	10	AIO	7	10
156	0	0	0	0	0	0	AIO	4	11	AIO	7	11
157	0	0	0	0	0	0	AIO	4	12	AIO	7	12
158	0	0	0	0	0	0	AIO	5	9	0	0	0
159	0	0	0	0	0	0	AIO	5	10	0	0	0
160	0	0	0	0	0	0	AIO	5	11	0	0	0
161	0	0	0	0	0	0	AIO	5	12	0	0	0
162	0	0	0	0	0	0	AIO	6	9	0	0	0
163	0	0	0	0	0	0	AIO	6	10	0	0	0
164	0	0	0	0	0	0	AIO	6	11	0	0	0
165	0	0	0	0	0	0	AIO	6	12	0	0	0
166	0	0	0	0	0	0	AIO	7	9	0	0	0
167	0	0	0	0	0	0	AIO	7	10	0	0	0
168	0	0	0	0	0	0	AIO	7	11	0	0	0
169	0	0	0	0	0	0	AIO	7	12	0	0	0
170	0	0	0	0	0	0	AIO	1	13	0	0	0
171	0	0	0	0	0	0	AIO	1	14	0	0	0
172	0	0	0	0	0	0	AIO	1	15	0	0	0
173	0	0	0	0	0	0	AIO	1	16	0	0	0
174	0	0	0	0	0	0	AIO	2	13	0	0	0
175	0	0	0	0	0	0	AIO	2	14	0	0	0
176	0	0	0	0	0	0	AIO	2	15	0	0	0
177	0	0	0	0	0	0	AIO	2	16	0	0	0
178	0	0	0	0	0	0	AIO	3	13	0	0	0
179	0	0	0	0	0	0	AIO	3	14	0	0	0
180	0	0	0	0	0	0	AIO	3	15	0	0	0
181	0	0	0	0	0	0	AIO	3	16	0	0	0
182	0	0	0	0	0	0	AIO	4	13	0	0	0
183	0	0	0	0	0	0	AIO	4	14	0	0	0
184	0	0	0	0	0	0	AIO	4	15	0	0	0
185	0	0	0	0	0	0	AIO	4	16	0	0	0
186	0	0	0	0	0	0	AIO	5	13	0	0	0
187	0	0	0	0	0	0	AIO	5	14	0	0	0
188	0	0	0	0	0	0	AIO	5	15	0	0	0
189	0	0	0	0	0	0	AIO	5	16	0	0	0
190	0	0	0	0	0	0	AIO	6	13	0	0	0
191	0	0	0	0	0	0	AIO	6	14	0	0	0
192	0	0	0	0	0	0	AIO	6	15	0	0	0
193	0	0	0	0	0	0	AIO	6	16	0	0	0
194	0	0	0	0	0	0	AIO	7	13	0	0	0
195	0	0	0	0	0	0	AIO	7	14	0	0	0
196	0	0	0	0	0	0	AIO	7	15	0	0	0
197	0	0	0	0	0	0	AIO	7	16	0	0	0
198	0	0	0	0	0	0	0	0	0	0	0	0
199	0	0	0	0	0	0	0	0	0	0	0	0
200	0	0	0	0	0	0	0	0	0	0	0	0

268	0	0	0	0	0	0	0	0	0	0	0	0
269	0	0	0	0	0	0	0	0	0	0	0	0
270	0	0	0	0	0	0	0	0	0	0	0	0
271	0	0	0	0	0	0	0	0	0	0	0	0
272	0	0	0	0	0	0	0	0	0	0	0	0
273	0	0	0	0	0	0	0	0	0	0	0	0
274	0	0	0	0	0	0	0	0	0	0	0	0
275	0	0	0	0	0	0	0	0	0	0	0	0
276	0	0	0	0	0	0	0	0	0	0	0	0
277	0	0	0	0	0	0	0	0	0	0	0	0
278	0	0	0	0	0	0	0	0	0	0	0	0
279	0	0	0	0	0	0	0	0	0	0	0	0
280	0	0	0	0	0	0	0	0	0	0	0	0
281	0	0	0	0	0	0	0	0	0	0	0	0
282	0	0	0	0	0	0	0	0	0	0	0	0
283	0	0	0	0	0	0	0	0	0	0	0	0
284	0	0	0	0	0	0	0	0	0	0	0	0
285	0	0	0	0	0	0	0	0	0	0	0	0
286	0	0	0	0	0	0	0	0	0	0	0	0
287	0	0	0	0	0	0	0	0	0	0	0	0
288	0	0	0	0	0	0	0	0	0	0	0	0
289	0	0	0	0	0	0	0	0	0	0	0	0
290	0	0	0	0	0	0	0	0	0	0	0	0
291	0	0	0	0	0	0	0	0	0	0	0	0
292	0	0	0	0	0	0	0	0	0	0	0	0
293	0	0	0	0	0	0	0	0	0	0	0	0
294	0	0	0	0	0	0	0	0	0	0	0	0
295	0	0	0	0	0	0	0	0	0	0	0	0
296	0	0	0	0	0	0	0	0	0	0	0	0
297	0	0	0	0	0	0	0	0	0	0	0	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0
	0